## Requirements
Number | Functional Area | Capability | Requirement | Must Have | Nice to Have
1.01 | Business | Compliance | Respondent must provide CETA compliant resource(s) | ü
1.02 | Business | Performance | Respondent must acknowledge that PSE may implement financial penalties for non-performance of kW / kWh targets | ü
1.03 | Business | Planned outage | Respondent must provide PSE 7 days advanced notice for any planned outage | ü
1.04 | Business | Planned outage | Respondent must provide PSE 7 days advanced notice for any testing | ü
1.05 | Business | Compliance | Respondent must comply with all applicable laws and regulations. Respondent must ensure that all proposed resources comply with all applicable PSE, WA state, and national safety standards. As applicable, respondent must support PSE's compliance with privacy laws and regulations including WAC 480-100-153 and WAC 480-90-153. | ü
1.06 | Business | Sale of information | Respondent must not sell any customer information obtained from PSE or from the customer through PSE programs. | ü
2.01 | Engineering | Asset Management | Respondent must provide the physical location of the resource allowing PSE to match it with the transmiission or distribution system. It is assumed and expected that the vendor/supplier of the project will provide the GIS coordinate data to PSE in electronic form. | ü
2.02 | Engineering | Asset Management | Respondent must provide resource nameplate, resource availability, and response information to PSE. | ü
2.03 | Engineering | Communications | Respondent requested to be capable of communicating using the following: -Standards and protocols: IEEE 2030.5, DNP3 SCADA protocol devices, Modbus SCADA protocol devices, SunSpec Smart Inverter Profile (Modbus or DNP3), MESA Storage Profile (Modbus or DNP3), ICCP Respondent requested to describe experience with: -IEEE 2030.5: Describe communications experience with IEEE 2030.5 and specify equipments (i.e. battery controller, inverter, etc) controlled by the IEEE signal | ü
2.04 | Engineering | Communications | Respondent requested to validate that the resource can communicate using real-time data with IEEE 2030.5 or DNP 3.0 communication standards, etc. What PCS (Power Control System) and Inverter equipment did you communicate with (i.e., battery controller, inverter, both)? Were Watch Dog Timers and diagnostics used if communication failures occured? | ü
2.05 | Engineering | Grid Operation | Respondent must adhere to all applicable PSE technical specifications and open industry communication standards, as follows: -Technical Specifications for jurisdictional Large and Small Generation Interconnection, non-jurisdictional Small Generation Interconnection, and Load and Transmission Interconnection, that outline the standards needed to interconnect (http://www.oasis.oati.com/psei/index.html) -IEEE 1547-2018: Standard for Interconnection and Interoperatbility of Distributed Energy Resources with Associated Electric Power System Interfaces (https://standards.ieee.org/products-services/standards-related/pdf/electric-power-systems.html) IEEE 2800-2022: IEEE Standard for Interconnection and Interoperability of Inverter-Based Resources (IBRs) Interconnecting with Associated Transmission Electric Power Systems -PSE's Technical Specification and Operating Procedures for Interconnection of Generation Facilities Not Subject to FERC Jurisdiction (https://www.oasis.oati.com/woa/docs/PSEI/PSEIdocs/PSE-ET-160.70_NonFERC_19Aug07.pdf) | ü
2.06 | Engineering | Inverter | Respondent must provide inverter specifications to PSE including, but not limited to: -Rated AC output power, current, and voltage; -Power factor range of adjustability; -Available voltage and frequency protective elements; -Available grid support functions (anti-islanding, voltage ride through, voltage support, etc.); -Available communication protocols; -Grid standard (IEEE 1547, IEEE 2800, and UL1741) compliance information | ü
3.01 | IT | Cybersecurity | Respondent must meet industry best practices for security standards set by NIST-IR 7628 | ü
3.02 | IT | Cybersecurity | Respondent shall remove or disable all software components that are not required for the operation and maintenance of the device prior to the Factory Acceptance Testing (FAT). The Respondent shall provide documentation on what is removed and/or disabled | ü
3.03 | IT | Cybersecurity | Respondent shall provide, within a pre-negotiated period, appropriate software and service updates and/or workarounds to mitigate all vulnerabilities associated with the product and to maintain the established level of system security | ü
3.04 | IT | Cybersecurity | Respondent shall certify that its systems and products have undergone cyber security testing by leading and independent government sanctioned organizations | ü
3.05 | IT | Cybersecurity | After contract award, the Respondent shall provide notification of known security vulnerabilities affecting the Respondent supplied or required operating system, application and critical third-party software within a pre-negotiated period after public disclosure | ü
3.06 | IT | Cybersecurity | After contract award, the Respondent shall provide notification of a patch(es) affecting security within a pre-negotiated period, as identified in the patch management process. The Respondent shall apply, test and validate the appropriate updates and/or workarounds on a baseline reference system before distribution. Mitigation of these vulnerabilities shall occur within a pre-negotiated period | ü
3.07 | IT | Data security | Respondent must comply with PSE's Security Addendum (Consultant or Hosted) and ensure data security for all relevant usage, metering, settlement, and customer information. | ü
3.08 | IT | Standards | Respondent requested that system be capable of fully complying with and capable of communicating to the resource (PV + storage or BESS) using a smart inverter with its PCS system. PSE requires that the Smart Inverter incorporate or embed into its controls the SunSpec interoperability standards. These standards and communication protocols shall be as follows: * IEEE 2030.5 * DNP3.0 * Modbus TCP The above communication protocols shall provide open interoperability and real-time communication to the PCS control system and components which the Smart Inverter is part of the controls equipment. Security with the Smart Inverter shall also include: PSE security requirements, TLS, PKI infrastructure, Digital Certificates and authority, encryption (SHA-256), authenication, authorization, indentities, and client identification with the above communications. The Sunspec Standard shall provide a Device Information Data Model to collect, read, and write data to the Smart Inverter. This shall consist of CSIP profile for the inveter, monitoring power production data (kWH, kW, Delivered, Received, charging ramp rates, alarms, chargeing schedules, events, over/under voltage, over/under current, Frequeny, and all power-voltage imbalances). It shall also provide connect and disconnect functions, High/low voltage ride through, Volt-Var, and PF control functions. PSE requires reporting data capabilities as well with Real and Reactive Power, Volts, Amps, Hz, and PF for all 3 phases + Neutral including Averages. |  | ü
4.01 | Load Office | Control | Resources must be capable of connecting to PSE’s system with monitoring and control through PSE’s SCADA. | ü
4.02 | Load Office | Dispatch | Supplier/Respondent must have the capability with its resource site controls to indicate resource availability, readiness, and equipment states of all components to dispatch the resource. | ü
4.03 | Load Office | Dispatch | Respondent required to have capability to dispatch capacity whenever required by PSE for system support. | ü
5.01 | Operations | Alarms | Supplier/Respondent shall have the ability to provide controls which manage all states, alarms and events to PSE. | ü
5.02 | Operations | Control | Supplier/ Respondent shall have the capability to respond to real time control from PSE to the resource PCS controls (site). PSE shall have the ability to perform read request, respond and write data including all PCS configuration controller data. | ü
5.03 | Operations | Event response | Supplier/ Respondent shall provide the time window (i.e., minutes/seconds/milliseconds) for responding to a PSE dispatchable event. | ü
5.04 | Operations | Event response | Respondent must be able to receive event notifications from PSE. | ü
5.05 | Operations | Event response | Respondent shall describe their notification requirements in order to successfully respond to an event. | ü
5.06 | Operations | Ride-through | Respondent must ensure that inverters ride-through momentary outages according to standard IEEE 1547 -2018 and IEEE 2800, standard CA-21, and standard UL-1741. | ü
5.07 | Operations | SCADA | Respondent is required to provide interconnection architecture (building upon included diagrams and including more detail) that shows the connectivity with meter, resource, utility service point, transformer highlighting the energy flow, and the communication standards used to communicate between the devices. | ü
5.08 | Operations | SCADA | Respondent must provide uptime availability for monitoring, control, and metering purposes to the PSE SCADA system. | ü
5.09 | Operations | SCADA | Respondent must provide communication status of monitoring, control, dispatch link. | ü
5.1 | Operations | SCADA | Respondent must be able to curtail resource when instructed by PSE. | ü
5.11 | Operations | SCADA | Respondent must provide digital and analog points for SCADA. | ü
5.12 | Operations | SCADA | Respondent must provide status, performance, and configuration data. | ü
5.13 | Operations | Maintenance | For any response with a PSE ownership option, Respondent shall provide equipment maintenance requirements. | ü