## DSS RFP Inbox Q&As
| 2025 DSS RFP Q&A through | solarstoragerfpmailbox@pse.com
# | Question/comment to be posted on website | PSE response
1 | To align our design and pricing precisely with PSE’s operational expectations, we respectfully request guidance on the following: 1. Optimal Capacity Envelope — Would a 2 MW / 4-hour (≈ 8 MWh) configuration be optimal for feeders associated with the Bonney Lake and Longmire substations, or would a slightly higher-duration system (e.g., 2 MW / 6–8 hour) provide greater benefit to PSE’s distribution operations? Confirmation of the preferred capacity band will enable us to right-size the system to available hosting capacity and operational needs. 2. Co-Location Feasibility — Based on current hosting capacity and distribution planning data, could PSE indicate whether any existing PSE-owned or contracted solar PV site may accommodate such a BESS addition under the Build-Transfer structure? This would allow us to focus engineering and financial modeling on the most appropriate site and substation feeder. 3. Technology / OEM Pre-Approval — To ensure technical compliance and bankability, we request confirmation that the following Tier-1 BESS manufacturers and their current product families (or equivalent systems meeting the same performance standards) are acceptable to PSE under Exhibit C (Approved Equivalent): • GE Vernova – Reservoir Series • Fluence Energy – GridStack / Ultrastack • Tesla Energy – Megapack 2XL • Eos Energy Enterprises – Znyth aqueous zinc system • Powin Energy – Stack 750 / Centipede platform • EnerVenue – Nickel-Hydrogen container modules • LG Energy Solution – ESS LFP Rack Systems • Samsung SDI – Containerized Energy Storage System Series • EVO Storage Systems – GenX LFP container series We would also appreciate PSE’s confirmation that “or equivalent” systems meeting the same UL 9540A and NFPA 855 criteria may be considered acceptable for proposal purposes. | 1. Optimal Capacity Envelope — Would a 2 MW / 4-hour (≈ 8 MWh) configuration be optimal for feeders associated with the Bonney Lake and Longmire substations, or would a slightly higher-duration system (e.g., 2 MW / 6–8 hour) provide greater benefit to PSE’s distribution operations? Confirmation of the preferred capacity band will enable us to right-size the system to available hosting capacity and operational needs. All pertinent information is provided in the RFP documents and BESS sizing is dependent on each specific feeder. 2. Co-Location Feasibility — Based on current hosting capacity and distribution planning data, could PSE indicate whether any existing PSE-owned or contracted solar PV site may accommodate such a BESS addition under the Build-Transfer structure? This would allow us to focus engineering and financial modeling on the most appropriate site and substation feeder. There are no existing PSE owned PV sites in the Bonney Lake or Longmire that can accommodate a BESS facility. 3. Technology / OEM Pre-Approval — To ensure technical compliance and bankability, we request confirmation that the following Tier-1 BESS manufacturers and their current product families (or equivalent systems meeting the same performance standards) are acceptable to PSE under Exhibit C (Approved Equivalent): The OEMs listed are recognized Tier-1 manufacturers, but we cannot speak to the specific models at this time. This mailbox correspondence is just for general RFP questions and will not delve into detailed evaluation specific questions. Any questions or concerns regarding tech specs and similar matters will be addressed later by the evaluation team.
2 | I have a question now about the quantitative metrics and price score. I understand that PSE uses BCA analysis to evaluate projects. What is the result of this analysis? Is it a ranking of projects from best to worst? If so, how is that combined with the qualitative score? | We have a ranking of best to worst projects that includes the qualitative analysis in it, though that portion is weighted 40% compared to the price which is weighted 60%. However, another element we take into account too is if the project is cost effective per our cost test ratios (societal cost test and total resource cost test). A project can be ranked highly, but not be cost effective, in which case we would not short list it.
3 | We respectfully requests PSE’s guidance on whether any of the following PSE-owned generating or substation facilities may have surplus or developable land appropriate for a BESS installation: • Baker River Hydroelectric Complex (Upper and Lower Baker Dams) • Whitehorn and Fredonia Gas Generating Stations • Snoqualmie Falls Hydroelectric Plant • Encogen Cogeneration Facility • Wild Horse Wind and Solar Facility (Kittitas County) • Hopkins Ridge Wind Facility (Columbia County) In the event that no PSE-owned surplus land is available at these or other sites, JSD will identify and secure private parcels adjacent to PSE’s generating or substation facilities, ensuring proximity to existing feeders, interconnection access, and compatible zoning. | PSE does not have available land at the sites listed below for development.
4 | Thanks for this heads-up, as well as the follow-up about expedited solar procurement. We have three questions about specific projects under development: 1. We have a 5 MW solar site in Kittitas County, but understand that PSE has concerns about added solar generation in Kittitas. We initially planned to colocate storage to mitigate these concerns, but the latest notice on solar asked for solar-only projects. Would PSE be open to solar-only projects in Kittitas, and/or would you recommend bidding in a hybrid project instead? 2. We have a 5 MW BESS site near the South Hill substation, and noted that the feeder adjacent to the site has zero MW in the sub's queue. However, the feeder connecting to that sub from the south has 5.1 MW in the sub's queue. We expected that any feeder connecting to the same sub would have the same "sub queued MW", but that isn't true in this case. Could you confirm that this data is accurate, and therefore that the feeder adjacent to the property would be evaluated without any queued MW on the sub? 3. Similar question at the BERTHUSEN sub in Lynden (Whatcom county) -- we're in discussion with the owners next to that sub. The adjacent overhead feeder has 4.7 queued MW at the sub, but the adjacent underground feeder has zero queued MW at the sub. This is similarly unexpected behavior, so we just wanted to confirm this is correct. | Thank you for your interest in PSE’s DSS RFP, the answers to your questions are below: 1. As stated in the RFP, PSE’s cross-Cascades transmission path, the Intermountain Power (“IP”) line, which crosses the Cascade Mountains to Kittitas County is fully subscribed. System upgrade costs from previously proposed distributed renewable projects in Kittitas County have proven to be cost-prohibitive because they trigger an upgrade to the IP line. PSE expects that solar projects proposed in Kittitas County will likely result in the same cost-prohibitive system upgrades, which are unrelated to the interconnection cost estimates listed on the following page and true-up language in the draft pro forma contracts. However, PSE will still consider and evaluate projects proposed in the Kittitas region. 2. & 3. Thank you for pointing this out, our HCA team is investigating the issue. We will give you an update they come to a conclusion.
5 | The posted Draft Prototype Design-Build-Transfer Agreement contemplates the Developer performing all construction activities and transferring the completed system to PSE at Final Completion. Would PSE be open to an alternative arrangement under which the Developer completes all development activities (including site control, permitting, interconnection, design, and equipment selection) and then transfers a fully “shovel-ready” project to PSE prior to the start of construction, with PSE (or its designated EPC) assuming responsibility for construction and commissioning? This “Development-Transfer” structure would achieve the same outcome of PSE ownership of the completed System while allowing PSE to manage construction directly under its preferred labor, safety, and contracting standards. | PSE is open to the option of a milestone payment structure, providing funding for key project developments. However, we expect the construction scope to be included in any offer provided. An EPC contractor should already be identified in any ownership proposal provided. We understand the contractor could change through development and negotiations, but we expect the price to remain the same or improve with any contractor adjustment.
6 | Does PSE expect that BESS projects proposed in Kittitas County will also result in cost-prohibitive system upgrades? | PSE’s Grid-Mod team is currently working on an initiative in Kittitas and your project would need to be studied in parallel with their work. If you provide a project in the area we will review it, but we do not know at this time what the results will be.
7 | We'll plan to bid in both a solar+storage and a storage-only option in Kittitas, and will wait until Jan 30 because the rolling solar bid process starting Oct 30 is solar-only. Please let us know if PSE would be open to a solar+storage bid starting Oct 30. We have a separate question on the Longmire sub as well. We understand that capacity on this sub is a particular focus for this RFP, however, many feeders coming off that sub have 5.40 MW in the sub's queue. Considering the "Energy Delivery" scoring criteria, a project would lose points due to the MW in queue at the sub. We also understand that, per the main RFP document, "the same evaluation process will be used as the system wide process, but offers submitted to the targeted substation capacity solicitation will only be compared amongst themselves, separately from the system wide solicitation." Normally we would avoid bidding in projects where the POI has 5.4 MW queued on the sub, but because of the particular focus in the RFP on the Longmire sub, we plan to make an exception here. Are we thinking about this correctly? I realize this is related to our previous questions about the "Generation in Queue (Sub.)" variable, which your team is currently looking to, but just wanted to voice that observation about the Longmire sub's feeders. | Sounds good, thanks. We'll plan to bid in both a solar+storage and a storage-only option in Kittitas, and will wait until Jan 30 because the rolling solar bid process starting Oct 30 is solar-only. Please let us know if PSE would be open to a solar+storage bid starting Oct 30. We won’t be reviewing BESS projects in our new expedited process since it requires more due diligence in investigating safety, community impact and IX scope. You can submit a storage bid as early as October 30th, but it will be processed under our normal procedure and not through the expedited process. We have a separate question on the Longmire sub as well. We understand that capacity on this sub is a particular focus for this RFP, however, many feeders coming off that sub have 5.40 MW in the sub's queue. Considering the "Energy Delivery" scoring criteria, a project would lose points due to the MW in queue at the sub. We also understand that, per the main RFP document, "the same evaluation process will be used as the system wide process, but offers submitted to the targeted substation capacity solicitation will only be compared amongst themselves, separately from the system wide solicitation." The substation need for both Longmire and Bonney is the minimum of the BESS sizing requirements (2 MWs, 8 MWhs). We are allowing over sizing for these sites due to scaling benefits. However per the Exhibit A scoring rubric you referenced above, projects that are oversized compared to the feeder will receive less points in their evaluation. Normally we would avoid bidding in projects where the POI has 5.4 MW queued on the sub, but because of the particular focus in the RFP on the Longmire sub, we plan to make an exception here. Are we thinking about this correctly? I realize this is related to our previous questions about the "Generation in Queue (Sub.)" variable, which your team is currently looking to, but just wanted to voice that observation about the Longmire sub's feeders.
8 | We have a handful of questions regarding the recently-issued RFP. • Can inverters be de-rated for solar projects or hybrid solar+BESS projects? Table 2 “Resource Types” on PDF Page 12 of the RFP only notes the de-rating prohibition for BESS. • Does a lease (not an option to lease, but an actual lease) count as “Site Control Complete” (3 points) under the Site Control score section or only ownership of the land? • Under the Equity Rubric, are points only available for projects located in – and with positive impacts to – vulnerable populations scored as “high” in the Named Communities tool? That is, being in a location scored as “Medium” for Vulnerable Population is not eligible for these points? • Under the Equity Rubric, it appears that projects located in areas with both Highly-Impacted Communities and in a “High” Vulnerable Population level will obtain more points than projects located in either an HIC or High VP area. Is that correct? • Is PSE interested in bids that offer additional grid resilience benefits such as black-start capability, grid-forming inverters, or similar benefits beyond what is otherwise required in the RFP? • Is PSE requiring a site-specific Hazard Mitigation Analysis (HMA) for BESS (per PDF Page 16 of the RFP document) or may a more generic OEM-developed HMA for their equipment be used in order to be deemed to have a conforming proposal? High-quality, site-specific HMAs tend to cost around $25,000 each and may serve as a barrier to certain bidders. • For PSE Ownership: o PSE is requesting that bidder provide a proposal for an LTSA. Is PSE expecting that the LTSA will be priced separately from the purchase price of the project? o Will the price of the LTSA impact a project’s / bid’s score or simply be used to determine whether PSE will out-source maintenance activities versus in-sourcing those activities? | We have a handful of questions regarding the recently-issued RFP. • Can inverters be de-rated for solar projects or hybrid solar+BESS projects? Table 2 “Resource Types” on PDF Page 12 of the RFP only notes the de-rating prohibition for BESS. PSE will not accept de-rated inverters for solar and hybrid projects. This requirement is coming from our interconnection team. • Does a lease (not an option to lease, but an actual lease) count as “Site Control Complete” (3 points) under the Site Control score section or only ownership of the land? A fully executed lease agreement would count as complete site control. • Under the Equity Rubric, are points only available for projects located in – and with positive impacts to – vulnerable populations scored as “high” in the Named Communities tool? That is, being in a location scored as “Medium” for Vulnerable Population is not eligible for these points? Projects not located within high-ranked Vulnerable Populations, Highly Impacted Communities or a combination of the two may still be eligible for points in the equity rubric depending on the question, but will not receive points if the question is specifically for Named Communities. To further clarify what Named Communities encompass, a low or medium ranked Vulnerable Population is not a Named Community unless it overlaps with a Highly Impacted Community. • Under the Equity Rubric, it appears that projects located in areas with both Highly-Impacted Communities and in a “High” Vulnerable Population level will obtain more points than projects located in either an HIC or High VP area. Is that correct? Yes, locating a project in both a VP and HIC will obtain more points, than solely in either. • Is PSE interested in bids that offer additional grid resilience benefits such as black-start capability, grid-forming inverters, or similar benefits beyond what is otherwise required in the RFP? At this time PSE is unsure it will be able to implement additional use cases from BESS resources. We are looking into expanding use cases in future RFPs, but this current RFP will not provide additional points or value for increased resilience. • Is PSE requiring a site-specific Hazard Mitigation Analysis (HMA) for BESS (per PDF Page 16 of the RFP document) or may a more generic OEM-developed HMA for their equipment be used in order to be deemed to have a conforming proposal? High-quality, site-specific HMAs tend to cost around $25,000 each and may serve as a barrier to certain bidders. A generic OEM developed HMA is acceptable for the initial proposal. If a project is shortlisted, during the permitting and development process a site specific HMA could be required by either the AHJ or PSE. • For PSE Ownership: o PSE is requesting that bidder provide a proposal for an LTSA. Is PSE expecting that the LTSA will be priced separately from the purchase price of the project? Provide the LTSA pricing in Exhibit B, tab 8 “Ownership – Operating Costs” in one of the Service Agreement line items. The LTSA cost should be separate from the upfront fixed cost of ownership. o Will the price of the LTSA impact a project’s / bid’s score or simply be used to determine whether PSE will out-source maintenance activities versus in-sourcing those activities? The LTSA pricing will be evaluated with the project offer to determine overall cost-effectiveness.
9 | I am writing with a question about the 2025 PSE DSS RFP. Will PSE accept more than one submission on the same parcel of land? The projects in question would not intersect; that is, it is physically feasible to construct both projects. | It’s fine to submit two projects to the same parcel, but if they are entirely different proposals then each will need its own submission materials. If they are being proposed as a combined project, such as a solar and storage coupled project, then one submission is fine.
10 | Is there a requirement to submit a Notice of Intent (NOI) form to participate in this RFP. We do not see one, but want to confirm that there is no such requirement to participate in this RFP iteration. We know other utilities often require these. | Do you mean a notice of intent as a respondent to the RFP? We do not require that, only the documents listed in Section 5. are required, as well as the signed Bid Certificate in Exhibit B tab 9.
11 | We're working on Exhibit B for a couple of solar projects. A few questions related to that or the RFP more generally: • Cost-Effectiveness: Does location of a project in a Named Community affect the quantitative portion of the score / the cost-effectiveness baseline, where presence in one of those communities shows as having more value to PSE? • PSE Self-Bids: Does PSE intend to bid its own projects / land into either the System-Wide RFP and/or the Target Substation Capacity RFP? If yes, is PSE interested in working with outside developers on the development of these projects? • Build-Transfer Tax Credits: Does PSE have the ability to claim / monetize tax credits or should that be done on the developer side? • Build-Transfer Spare Parts: Does PSE have a desire for a specific spare parts level / program? • Easements: o If an easement is required along a public road / ROW, would PSE obtain the easement or would it be the responsibility of the developer? (we understand a private ROW easement is the responsibility of the developer) o If a project requires an easement for a gen-tie / distribution line extension in order to work, must that easement be secured by the bid deadline per Row 47 of Exhibit B's "3. Facility" tab? | • Cost-Effectiveness: Does location of a project in a Named Community affect the quantitative portion of the score / the cost-effectiveness baseline, where presence in one of those communities shows as having more value to PSE? • The quantitative scoring is not impacted by a project’s location in a named community. • PSE Self-Bids: Does PSE intend to bid its own projects / land into either the System-Wide RFP and/or the Target Substation Capacity RFP? If yes, is PSE interested in working with outside developers on the development of these projects? • PSE will not be bidding in its own projects or land for development, nor partnering with developers in this RFP. • Build-Transfer Tax Credits: Does PSE have the ability to claim / monetize tax credits or should that be done on the developer side? • Tax credit monetization on our side is a bit more complicated. Generally developers monetize it for their proposals and it’s simpler for us. • Build-Transfer Spare Parts: Does PSE have a desire for a specific spare parts level / program? • There is no specific strategy for spare parts. During the evaluation, PSE will potentially be holding technical interviews with respondents and this would be a good question to bring up. • Easements: o If an easement is required along a public road / ROW, would PSE obtain the easement or would it be the responsibility of the developer? (we understand a private ROW easement is the responsibility of the developer) It depends and a concrete answer cannot be given without real estate reviewing the specific case. In general, if it’s along a public road, it might fall under PSE's franchise if it is PSE infrastructure. o If a project requires an easement for a gen-tie / distribution line extension in order to work, must that easement be secured by the bid deadline per Row 47 of Exhibit B's "3. Facility" tab? Gen-tie easements are not required to be secured by the bid deadline.
12 | We noticed that the Longmire substation has 5.4 MW queued on it at the sub level. Given the special attention on that sub in the RFP, we wanted to check whether the queued MW on that sub will affect procurement there? For example, compared to the Bonney Lake sub, which has no queued MW at the sub, should we expect a difference in procurement between the two? | There are some recent generation projects queued for that substation, however that won’t impact the overall procurement for Longmire. PSE needs a storage resource at that site and projects applying for any of the Targeted Substation Capacity sites won’t be competing with other assets only applying for the service territory wide option. When looking for potential feeders, just compare the feeder’s hosting capacity with what is already queued on the circuit, don’t worry about the sub’s current rating.
13 | I would like to submit the following questions to the Q&A for the 2025 DSS RFP. Questions: • When can we expect answers? Is there one big Q&A, or will they be coming out weekly? • Does the IX estimate include fiber costs? • What is your COD preference? • General equipment questions: o Is the MWac size of the project determined by the hardware (inverter) nameplate rating or can the EMS limit the output to our desired MWac rating? o Are there any acceptable approaches that would allow us to oversize the BESS system without increasing the MWac size of the project?  If equipment ships out of the factory with a nameplate that reflects a lower-than-marketed rating, is that acceptable?  Alternate datasheet at reduced rating or product certificate from supplier?  Any other options or guidance on how this requirement applies to the MWac size of a BESS project for this RFP? o If the Inverter manufacturer supplies the inverter with a nameplate that reflects a reduced capacity compared to the off-the-shelf product, is that acceptable? What if they provide a datasheet or certificate for that reduced size? • Specific to Tesla: o Tesla allows you to select MegaPack configurations with specific power ratings that differ from the rating on the general product datasheet. For example, if the 500kVA configurations is selected, the MegaPack nameplate will show a Maximum Continuous Power rating of 500kVA.  Could a 4MWac project include 8x MegaPacks (500kVA nameplate - but datasheet rating is higher), or would this go against the “Inverter nameplate cannot be factory or firmware derated” requirement? | I would like to submit the following questions to the Q&A for the 2025 DSS RFP. Questions: • When can we expect answers? Is there one big Q&A, or will they be coming out weekly? We generally respond to questions to this mailbox within 2 BDs. On the RFP webpage (https://www.pse.com/en/pages/energy-supply/acquiring-energy/2025-Distributed-Solar-and-Storage-RFP), see snippet below, all bidder Q&As are posted publicly. The next update will be by the end of the month. • Does the IX estimate include fiber costs? The IX estimates provided in the RFP, snipped below, are an average of actual costs we’ve seen for similar sized projects, with some contingency added. Fiber was included in the analysis. • What is your COD preference? For projects applying to the service territory wide solicitation, end of year 2028 is our target. For projects applying to the Targeted Substation Capacity solicitation, end of year 2029 is our target. • General equipment questions: o Is the MWac size of the project determined by the hardware (inverter) nameplate rating or can the EMS limit the output to our desired MWac rating? The MW AC size of the inverter determines the nameplate rating. Our protection team will not consider EMS limited output as a viable option. o Are there any acceptable approaches that would allow us to oversize the BESS system without increasing the MWac size of the project?  If equipment ships out of the factory with a nameplate that reflects a lower-than-marketed rating, is that acceptable? Our protection team will not accept factory de-rated inverters.  Alternate datasheet at reduced rating or product certificate from supplier? Our protection team will require that the inverter size is per product cert.  Any other options or guidance on how this requirement applies to the MWac size of a BESS project for this RFP? Our recommendation is to size your project based on the incremental product specs. If your sizing incrementally goes from 5.8 MW AC to 6.2 MW AC. It is not a viable option to use derated inverters to achieve a 6 MW AC target from 6.2 MWs, just build your proposal around 5.8 MWs. o If the Inverter manufacturer supplies the inverter with a nameplate that reflects a reduced capacity compared to the off-the-shelf product, is that acceptable? What if they provide a datasheet or certificate for that reduced size? Our protection team has been very adamant about inverter ratings. They will not accept factory de-rated inverters. • Specific to Tesla: o Tesla allows you to select MegaPack configurations with specific power ratings that differ from the rating on the general product datasheet. For example, if the 500kVA configurations is selected, the MegaPack nameplate will show a Maximum Continuous Power rating of 500kVA.  Could a 4MWac project include 8x MegaPacks (500kVA nameplate - but datasheet rating is higher), or would this go against the “Inverter nameplate cannot be factory or firmware derated” requirement? We cannot speak for this Tesla specific use case. However, our protection team has been very adamant about inverter ratings. I would err on the side of caution.
14 | I have listed questions regarding the 2026 PSE RFP below: 1. Can you confirm the interconnection scope that the respondent is responsible for? 2. What type of upgrades do the interconnection cost estimates assume in each system size tier? 3. Is hosting capacity being taken into account in the published interconnection cost ranges? For example, if there is hosting capacity available (based on the public PSE HCM), then why would a project sized under the current available capacity trigger such large cost estimates? 4. Does the request to stay below the available hosting capacity also apply to stand alone BESS? | 1. Can you confirm the interconnection scope that the respondent is responsible for? Typically the developer is responsible for everything interconnection wise from the PSE owned revenue meter to their generation facility. However, formal meetings with the interconnection team will better define that scope. Sometimes one party takes on all civil work to cut overall cost or procure certain equipment the other party is responsible for to help expedite delivery. 2. What type of upgrades do the interconnection cost estimates assume in each system size tier? The interconnection estimates provided in the RFP are an average of actual total project costs we’ve seen for similar sized projects, with contingency added. For example, with the largest tier of 4-6 MWs that cost includes projects that have triggered substation upgrades like smart breakers or other large cost items like dedicated feeders. The majority of projects in the 4-6 MW size range will not trigger those large upgrades, we’re just trying to take a conservative approach to overall costs. 3. Is hosting capacity being taken into account in the published interconnection cost ranges? For example, if there is hosting capacity available (based on the public PSE HCM), then why would a project sized under the current available capacity trigger such large cost estimates? The hosting capacity is not taken into account in the published interconnection cost range. The interconnection cost is based solely on historic projects in those size ranges. In a future HCA iteration we hope to have a mechanism in place that can give a preliminary interconnection estimate based on the local feeder/sub limitations, but we don’t have the capability currently. 4. Does the request to stay below the available hosting capacity also apply to stand alone BESS? Yes.
15 | I have one follow up question that will inform our finalized system sizes: Does PSE use the interconnection estimate averages in their RFP evaluation, or will project selection be based on more bespoke interconnection cost analyses? | In your proposal pricing you should include the estimated IX cost based on the appropriate project size, so it will be incorporated into the evaluation. Shortlisted proposals will then move onto negotiations and trigger specific studies for each site. After facility studies are complete, those results will then be included in each negotiated agreement.
16 | How does PSE prefer to interconnect DG BESS -- Pad-mounted or pole-mounted? If pole mounted, is there a minimum amount of poles required? | The default approach is usually to do the cheapest option, which is pole mounting. However, some jurisdictions don’t allow or frown upon OH equipment for aesthetic reasons. In those cases we will sometimes opt for a pad-mount. There is no minimum number of poles required. If the project is large enough it could trigger duplicative protections in place, like two reclosers that would each have their own poles. Designs can vary.
17 | Will PSE accept redlines to the Mutial NDA or the Customer Consent letter? (Exhibits D and J) | The Customer Consent letter just authorizes PSE to share information between firewalled departments if needed. If your concern is regarding the last sentence about posting on PSE’s OASIS website, this is not applicable to DSS RFP applicants since none of the projects are allowed to have transmission interconnections. You can provide edits to the mutual NDA, we just have to get our legal department’s approval.
18 | Can you describe the specific technical concerns that the protection team has with inverter factory derates, software derates, EMS limitations, etc. | There are safety concerns that de-rated inverters may be deployed to avoid essential system upgrades (i.e. protective relays and DTT) and a lack of confidence in the performance of de-rated inverters during fault conditions. Since PSE has limited experience with inverter-based technology, we cannot offer exceptions or change our internal standards at this time.
19 | Our team is narrowing in on final standalone BESS system sizes. Can you clarify whether the extra points for staying under the available hosting capacity take into account both existing interconnected projects and those currently in the queue? In other words, should we be subtracting any queued MW from the total available hosting capacity in order to maximize our points in that category? | Extra points are given for projects whose capacity is below the hosting capacity of the feeder minus what’s queued for interconnection, see snippet below. The hosting capacity already takes into account operational projects, the queue is for projects being processed in our Schedule 152 interconnection process.
20 | • For BTA's, the RFP mentions a full list of requirements that will be released by 1/30. Is there an updated timeframe on when this will come out? • Regarding Tab 3b. Can you provide Liquidated damages assumptions? • Regarding Tab 2b. o If we want to submit multiple bids for the same project, would you prefer a whole separate worksheet or can we add another duplicate tab to one spreadsheet for multiple project options. o Can you clarify line 70? Is this referring to recs and, would battery fall under N/A? | See answers in red below. • For BTA's, the RFP mentions a full list of requirements that will be released by 1/30. Is there an updated timeframe on when this will come out? Our DER engineering team is currently working on a BESS Design Requirements list for PSE ownership, we don’t have any updates on a date, but as development gets closer to release we will send an email out to our distribution list. • Regarding Tab 3b. Can you provide Liquidated damages assumptions? Can you elaborate a bit more? Are you talking about LDs for a BESS agreement (which is our version of a PPA for BESS) or BTA? • Regarding Tab 2b. o If we want to submit multiple bids for the same project, would you prefer a whole separate worksheet or can we add another duplicate tab to one spreadsheet for multiple project options. For organizational purposes we need a separate Exhibit B per variation. You can provide multiple iterations of the same project under one proposal, but please have a separate Exhibit B per variation and note in the file title the # variation. If you have any updates to those variations during the evaluation process, stick to the same naming convention when providing updates. o Can you clarify line 70? Is this referring to recs and, would battery fall under N/A? For line 70, RECs would be the best example of an environmental attribute and obviously not applicable to BESS. However, a provision in PSE’s BESS agreement is the requirement that PSE be entitled to all attributes regardless of when they come into existence, see section 12 of Exhibit G and there is a cost sharing mechanism in place too. While BESS does not have any environmental attributes like RECs at the moment, if federal or state policy was to change to include new attributes, PSE would be entitled to those. We expect proposals to acknowledge PSE’s entitlement of all potential attributes.
21 | We are evaluating the use of Tesla Megapack 2XL units for our potential submission to the 2025 DSS RFP and are seeking clarification on their acceptability under PSE’s requirements regarding inverter derating. The Megapack’s real and apparent power ratings can be permanently firmware-limited at the factory via option codes. These limits are irreversible and are reflected on both the internal nameplate label and the external enclosure label. For reference, we have attached a brief guide describing this configuration. We are requesting confirmation that this type of factory-applied, nameplate-reflected firmware limiting would be acceptable and not considered prohibited derating, given PSE’s stated position on inverter derating. | Our protection team has stated this firmware de-rating would not be acceptable.
22 | Can you provide any guidance of what is expected/ what is in a "Continuity of Business Plan". It is not referenced in the RFP, from my understanding. | It’s appreciated if you can provide a Continuity of Business plan, but not required for an RFP submittal. The plan is supposed to cover how your company will provide services during an emergency that may have short-term and long-term consequences. It’s not really applicable for these types of projects and more of a hold over from other RFPs for large scale utility projects.
23 | Thank you for the quick response! Are there any other placeholder documents that are not necessary for submission? | A Corporate Safety Plan, and Drug and Alcohol Plan is also just a nice to have, but not required. Everything else is pertinent.
24 | On the hosting capacity map, does the Generation Hosting Capacity take into account generation already in the queue? So in the example below, is there 3.2 MW available after the 5.4 MW in the queue connects, or if all 5.4 MW connects, would the circuit actually be over capacity? | The Generation Hosting Capacity does not take into account generation in queue, so this feeder is already overbooked.
25 | For the time being, we have a couple of questions about the Q&A process: 1. Is there a deadline for questions to be submitted? 2. When will answers to these questions be provided? 3. Will all answers to submitted questions be posted on the RFP website? | See answers below in red. 1. Is there a deadline for questions to be submitted? Questions can be submitted anytime leading up to the RFP submission deadline, January 30th, as well as after. 2. When will answers to these questions be provided? We generally answer directly to questions within two business days. 3. Will all answers to submitted questions be posted on the RFP website? Q&A is bundled monthly and submitted to the RFP webpage (2025-Distributed-Solar-and-Storage-RFP). The following link is the latest bundle, QA-Tracker.