## DSS RFP Inbox Q&As
|  | 2025 DSS RFP Q&A through | solarstoragerfpmailbox@pse.com
# | Date | Question/comment to be posted on website | PSE response
1 | 2025-10-06 | To align our design and pricing precisely with PSE’s operational expectations, we respectfully request guidance on the following: 1. Optimal Capacity Envelope — Would a 2 MW / 4-hour (≈ 8 MWh) configuration be optimal for feeders associated with the Bonney Lake and Longmire substations, or would a slightly higher-duration system (e.g., 2 MW / 6–8 hour) provide greater benefit to PSE’s distribution operations? Confirmation of the preferred capacity band will enable us to right-size the system to available hosting capacity and operational needs. 2. Co-Location Feasibility — Based on current hosting capacity and distribution planning data, could PSE indicate whether any existing PSE-owned or contracted solar PV site may accommodate such a BESS addition under the Build-Transfer structure? This would allow us to focus engineering and financial modeling on the most appropriate site and substation feeder. 3. Technology / OEM Pre-Approval — To ensure technical compliance and bankability, we request confirmation that the following Tier-1 BESS manufacturers and their current product families (or equivalent systems meeting the same performance standards) are acceptable to PSE under Exhibit C (Approved Equivalent): • GE Vernova – Reservoir Series • Fluence Energy – GridStack / Ultrastack • Tesla Energy – Megapack 2XL • Eos Energy Enterprises – Znyth aqueous zinc system • Powin Energy – Stack 750 / Centipede platform • EnerVenue – Nickel-Hydrogen container modules • LG Energy Solution – ESS LFP Rack Systems • Samsung SDI – Containerized Energy Storage System Series • EVO Storage Systems – GenX LFP container series We would also appreciate PSE’s confirmation that “or equivalent” systems meeting the same UL 9540A and NFPA 855 criteria may be considered acceptable for proposal purposes. | 1. Optimal Capacity Envelope — Would a 2 MW / 4-hour (≈ 8 MWh) configuration be optimal for feeders associated with the Bonney Lake and Longmire substations, or would a slightly higher-duration system (e.g., 2 MW / 6–8 hour) provide greater benefit to PSE’s distribution operations? Confirmation of the preferred capacity band will enable us to right-size the system to available hosting capacity and operational needs. All pertinent information is provided in the RFP documents and BESS sizing is dependent on each specific feeder. 2. Co-Location Feasibility — Based on current hosting capacity and distribution planning data, could PSE indicate whether any existing PSE-owned or contracted solar PV site may accommodate such a BESS addition under the Build-Transfer structure? This would allow us to focus engineering and financial modeling on the most appropriate site and substation feeder. There are no existing PSE owned PV sites in the Bonney Lake or Longmire that can accommodate a BESS facility. 3. Technology / OEM Pre-Approval — To ensure technical compliance and bankability, we request confirmation that the following Tier-1 BESS manufacturers and their current product families (or equivalent systems meeting the same performance standards) are acceptable to PSE under Exhibit C (Approved Equivalent): The OEMs listed are recognized Tier-1 manufacturers, but we cannot speak to the specific models at this time. This mailbox correspondence is just for general RFP questions and will not delve into detailed evaluation specific questions. Any questions or concerns regarding tech specs and similar matters will be addressed later by the evaluation team.
2 | 2025-10-07 | I have a question now about the quantitative metrics and price score. I understand that PSE uses BCA analysis to evaluate projects. What is the result of this analysis? Is it a ranking of projects from best to worst? If so, how is that combined with the qualitative score? | We have a ranking of best to worst projects that includes the qualitative analysis in it, though that portion is weighted 40% compared to the price which is weighted 60%. However, another element we take into account too is if the project is cost effective per our cost test ratios (societal cost test and total resource cost test). A project can be ranked highly, but not be cost effective, in which case we would not short list it.
3 | 2025-10-08 | We respectfully requests PSE’s guidance on whether any of the following PSE-owned generating or substation facilities may have surplus or developable land appropriate for a BESS installation: • Baker River Hydroelectric Complex (Upper and Lower Baker Dams) • Whitehorn and Fredonia Gas Generating Stations • Snoqualmie Falls Hydroelectric Plant • Encogen Cogeneration Facility • Wild Horse Wind and Solar Facility (Kittitas County) • Hopkins Ridge Wind Facility (Columbia County) In the event that no PSE-owned surplus land is available at these or other sites, JSD will identify and secure private parcels adjacent to PSE’s generating or substation facilities, ensuring proximity to existing feeders, interconnection access, and compatible zoning. | PSE does not have available land at the sites listed below for development.
4 | 2025-10-09 | Thanks for this heads-up, as well as the follow-up about expedited solar procurement. We have three questions about specific projects under development: 1. We have a 5 MW solar site in Kittitas County, but understand that PSE has concerns about added solar generation in Kittitas. We initially planned to colocate storage to mitigate these concerns, but the latest notice on solar asked for solar-only projects. Would PSE be open to solar-only projects in Kittitas, and/or would you recommend bidding in a hybrid project instead? 2. We have a 5 MW BESS site at near the South Hill substation, and noted that the feeder adjacent to the site has zero MW in the sub's queue. However, the feeder connecting to that sub from the south has 5.1 MW in the sub's queue. We expected that any feeder connecting to the same sub would have the same "sub queued MW", but that isn't true in this case. Could you confirm that this data is accurate, and therefore that the feeder adjacent to the property would be evaluated without any queued MW on the sub? 3. Similar question at the BERTHUSEN sub in Lynden (Whatcom county) -- we're in discussion with the owners next to that sub. The adjacent overhead feeder has 4.7 queued MW at the sub, but the adjacent underground feeder has zero queued MW at the sub. This is similarly unexpected behavior, so we just wanted to confirm this is correct. | Thank you for your interest in PSE’s DSS RFP, the answers to your questions are below: 1. As stated in the RFP, PSE’s cross-Cascades transmission path, the Intermountain Power (“IP”) line, which crosses the Cascade Mountains to Kittitas County is fully subscribed. System upgrade costs from previously proposed distributed renewable projects in Kittitas County have proven to be cost-prohibitive because they trigger an upgrade to the IP line. PSE expects that solar projects proposed in Kittitas County will likely result in the same cost-prohibitive system upgrades, which are unrelated to the interconnection cost estimates listed on the following page and true-up language in the draft pro forma contracts. However, PSE will still consider and evaluate projects proposed in the Kittitas region. 2. & 3. Thank you for pointing this out, our HCA team is investigating the issue. We will give you an update they come to a conclusion.
5 | 2025-10-10 | The posted Draft Prototype Design-Build-Transfer Agreement contemplates the Developer performing all construction activities and transferring the completed system to PSE at Final Completion. Would PSE be open to an alternative arrangement under which the Developer completes all development activities (including site control, permitting, interconnection, design, and equipment selection) and then transfers a fully “shovel-ready” project to PSE prior to the start of construction, with PSE (or its designated EPC) assuming responsibility for construction and commissioning? This “Development-Transfer” structure would achieve the same outcome of PSE ownership of the completed System while allowing PSE to manage construction directly under its preferred labor, safety, and contracting standards. | PSE is open to the option of a milestone payment structure, providing funding for key project developments. However, we expect the construction scope to be included in any offer provided. An EPC contractor should already be identified in any ownership proposal provided. We understand the contractor could change through development and negotiations, but we expect the price to remain the same or improve with any contractor adjustment.
6 | 2025-10-13 | Does PSE expect that BESS projects proposed in Kittitas County will also result in cost-prohibitive system upgrades? | PSE’s Grid-Mod team is currently working on an initiative in Kittitas and your project would need to be studied in parallel with their work. If you provide a project in the area we will review it, but we do not know at this time what the results will be.
7 | 2025-10-15 | We'll plan to bid in both a solar+storage and a storage-only option in Kittitas, and will wait until Jan 30 because the rolling solar bid process starting Oct 30 is solar-only. Please let us know if PSE would be open to a solar+storage bid starting Oct 30. We have a separate question on the Longmire sub as well. We understand that capacity on this sub is a particular focus for this RFP, however, many feeders coming off that sub have 5.40 MW in the sub's queue. Considering the "Energy Delivery" scoring criteria, a project would lose points due to the MW in queue at the sub. We also understand that, per the main RFP document, "the same evaluation process will be used as the system wide process, but offers submitted to the targeted substation capacity solicitation will only be compared amongst themselves, separately from the system wide solicitation." Normally we would avoid bidding in projects where the POI has 5.4 MW queued on the sub, but because of the particular focus in the RFP on the Longmire sub, we plan to make an exception here. Are we thinking about this correctly? I realize this is related to our previous questions about the "Generation in Queue (Sub.)" variable, which your team is currently looking to, but just wanted to voice that observation about the Longmire sub's feeders. | Sounds good, thanks. We'll plan to bid in both a solar+storage and a storage-only option in Kittitas, and will wait until Jan 30 because the rolling solar bid process starting Oct 30 is solar-only. Please let us know if PSE would be open to a solar+storage bid starting Oct 30. We won’t be reviewing BESS projects in our new expedited process since it requires more due diligence in investigating safety, community impact and IX scope. You can submit a storage bid as early as October 30th, but it will be processed under our normal procedure and not through the expedited process. We have a separate question on the Longmire sub as well. We understand that capacity on this sub is a particular focus for this RFP, however, many feeders coming off that sub have 5.40 MW in the sub's queue. Considering the "Energy Delivery" scoring criteria, a project would lose points due to the MW in queue at the sub. We also understand that, per the main RFP document, "the same evaluation process will be used as the system wide process, but offers submitted to the targeted substation capacity solicitation will only be compared amongst themselves, separately from the system wide solicitation." The substation need for both Longmire and Bonney is the minimum of the BESS sizing requirements (2 MWs, 8 MWhs). We are allowing over sizing for these sites due to scaling benefits. However per the Exhibit A scoring rubric you referenced above, projects that are oversized compared to the feeder will receive less points in their evaluation. Normally we would avoid bidding in projects where the POI has 5.4 MW queued on the sub, but because of the particular focus in the RFP on the Longmire sub, we plan to make an exception here. Are we thinking about this correctly? I realize this is related to our previous questions about the "Generation in Queue (Sub.)" variable, which your team is currently looking to, but just wanted to voice that observation about the Longmire sub's feeders.
8 | 2025-10-15 | We have a handful of questions regarding the recently-issued RFP. • Can inverters be de-rated for solar projects or hybrid solar+BESS projects? Table 2 “Resource Types” on PDF Page 12 of the RFP only notes the de-rating prohibition for BESS. • Does a lease (not an option to lease, but an actual lease) count as “Site Control Complete” (3 points) under the Site Control score section or only ownership of the land? • Under the Equity Rubric, are points only available for projects located in – and with positive impacts to – vulnerable populations scored as “high” in the Named Communities tool? That is, being in a location scored as “Medium” for Vulnerable Population is not eligible for these points? • Under the Equity Rubric, it appears that projects located in areas with both Highly-Impacted Communities and in a “High” Vulnerable Population level will obtain more points than projects located in either an HIC or High VP area. Is that correct? • Is PSE interested in bids that offer additional grid resilience benefits such as black-start capability, grid-forming inverters, or similar benefits beyond what is otherwise required in the RFP? • Is PSE requiring a site-specific Hazard Mitigation Analysis (HMA) for BESS (per PDF Page 16 of the RFP document) or may a more generic OEM-developed HMA for their equipment be used in order to be deemed to have a conforming proposal? High-quality, site-specific HMAs tend to cost around $25,000 each and may serve as a barrier to certain bidders. • For PSE Ownership: o PSE is requesting that bidder provide a proposal for an LTSA. Is PSE expecting that the LTSA will be priced separately from the purchase price of the project? o Will the price of the LTSA impact a project’s / bid’s score or simply be used to determine whether PSE will out-source maintenance activities versus in-sourcing those activities? | We have a handful of questions regarding the recently-issued RFP. • Can inverters be de-rated for solar projects or hybrid solar+BESS projects? Table 2 “Resource Types” on PDF Page 12 of the RFP only notes the de-rating prohibition for BESS. PSE will not accept de-rated inverters for solar and hybrid projects. This requirement is coming from our interconnection team. • Does a lease (not an option to lease, but an actual lease) count as “Site Control Complete” (3 points) under the Site Control score section or only ownership of the land? A fully executed lease agreement would count as complete site control. • Under the Equity Rubric, are points only available for projects located in – and with positive impacts to – vulnerable populations scored as “high” in the Named Communities tool? That is, being in a location scored as “Medium” for Vulnerable Population is not eligible for these points? Projects not located within high-ranked Vulnerable Populations, Highly Impacted Communities or a combination of the two may still be eligible for points in the equity rubric depending on the question, but will not receive points if the question is specifically for Named Communities. To further clarify what Named Communities encompass, a low or medium ranked Vulnerable Population is not a Named Community unless it overlaps with a Highly Impacted Community. • Under the Equity Rubric, it appears that projects located in areas with both Highly-Impacted Communities and in a “High” Vulnerable Population level will obtain more points than projects located in either an HIC or High VP area. Is that correct? Yes, locating a project in both a VP and HIC will obtain more points, than solely in either. • Is PSE interested in bids that offer additional grid resilience benefits such as black-start capability, grid-forming inverters, or similar benefits beyond what is otherwise required in the RFP? At this time PSE is unsure it will be able to implement additional use cases from BESS resources. We are looking into expanding use cases in future RFPs, but this current RFP will not provide additional points or value for increased resilience. • Is PSE requiring a site-specific Hazard Mitigation Analysis (HMA) for BESS (per PDF Page 16 of the RFP document) or may a more generic OEM-developed HMA for their equipment be used in order to be deemed to have a conforming proposal? High-quality, site-specific HMAs tend to cost around $25,000 each and may serve as a barrier to certain bidders. A generic OEM developed HMA is acceptable for the initial proposal. If a project is shortlisted, during the permitting and development process a site specific HMA could be required by either the AHJ or PSE. • For PSE Ownership: o PSE is requesting that bidder provide a proposal for an LTSA. Is PSE expecting that the LTSA will be priced separately from the purchase price of the project? Provide the LTSA pricing in Exhibit B, tab 8 “Ownership – Operating Costs” in one of the Service Agreement line items. The LTSA cost should be separate from the upfront fixed cost of ownership. o Will the price of the LTSA impact a project’s / bid’s score or simply be used to determine whether PSE will out-source maintenance activities versus in-sourcing those activities? The LTSA pricing will be evaluated with the project offer to determine overall cost-effectiveness.
9 | 2025-10-20 | I am writing with a question about the 2025 PSE DSS RFP. Will PSE accept more than one submission on the same parcel of land? The projects in question would not intersect; that is, it is physically feasible to construct both projects. | It’s fine to submit two projects to the same parcel, but if they are entirely different proposals then each will need its own submission materials. If they are being proposed as a combined project, such as a solar and storage coupled project, then one submission is fine.