## DSS RFP Inbox Q&As
|  | 2023 DSS RFP Q&A through | solarstorageRFPmailbox@pse.com
# | Date | Question/comment to be posted on website | PSE response
1 | 2023-10-10 | Good afternoon. I am interested in participating in the upcoming 2022 Distributed Solar and Energy Storage request for proposal. I am contacting you to inquire whether a water heater grid optimizer solution would qualify? Our water heater management solution provides convenience and intelligence so that consumers save money and enjoy hot water available whenever they need it. The system does more than securely monitor hot water usage and employ cost-saving demand management. It transforms the water heater into a grid storage asset that absorbs variations in renewable output, responds to real time changes in energy costs, and supports distribution reliability. | Thanks for the information. At the moment, PSE is only seeking front of the meter solutions for the DSS RFP, but as the RFP is finalized the resource parameters might change. Please wait for further RFP updates.
2 | 2023-10-10 | We build, design and install Microgrids comprised of micro-wind turbines, solar , storage and energy management systems. Please advise if we can participate in the RFP . | Your services sound applicable to the DSS RFP and we encourage you to apply when the final RFP is released.
3 | 2023-10-11 | I am inviting you to our virtual event so you can meet some of the diverse contractors. | Thank you for the invite. A representative from the DSS team won't be able to attend the virtual event, but we invite all applicable contractors to review and apply to our DSS RFP when it is finalized and filed. Your email address will be added to the distribution list.
4 | 2022-12-30 | Thanks for sending this RFP. We primarily work on BTM generation and storage, but have interconnected utility distribution and transmission level solar and storage. Four questions, 1. how can we access the PSE heatmap on ArcGIS? looks like we need a PSE account to retrieve this map. 2. Does PSE have a $/MWh target for solar, or $/kW-month price target for storage? 3. What is storage generation duration target? 4. What is the highest voltage interconnection PSE considers Distributed? | See responses to your questions below. 1. Sorry for the confusion, if you’re referring to page 5 in the RFP. The wrong link was provided and this link [PSE Heatmap (arcgis.com)] does not need a PSE account to access. You should be able to freely view the site after reading and agreeing to the terms and conditions that pop-up. However, this heat map is also currently being updated with final updates provided by January 23rd. 2. There is no target energy or capacity price for solar or storage. 3. PSE wants at least a four hour discharge per cycle. 4. All lines 12.5 kV and under are considered distribution.
5 | 2023-01-03 | Hello, your DSS RFP main document has a link in it pointing to pugetsoundenergy.maps.arcgis.com but it doesn’t work (page 5 of your doc). Seems to want a PSE employee email? Asks if you have an ARCGIS email and I created one to check it but it doesn’t allow that email to work either. Any help on getting access to the map from your RFP would be great. | Sorry for the confusion. The wrong link was provided and this link [https://pugetsoundenergy.maps.arcgis.com/apps/webappviewer/index.html?id=980fc190ffd648489a492f8363a1d2cc] does not need a PSE account to access. You should be able to freely view the site after reading and agreeing to the terms and conditions that pop-up. However, this heat map is also currently being updated with final updates provided by January 23rd.
6 | 2023-01-04 | Will there be an Interested Parties list for the 2023 RFP? Looking at the documents I believe our organization can support fire prevention within the BESS. | We will not be providing a list of bidders or interested parties participating in the RFP, but thanks for offering your services.
7 | 2023-01-04 | Also, I was wondering if PSE would be soliciting bids for third-party evaluations of these programs, and if these RFPs would also come through this distribution list or a separate list. | You have been added to the distribution list. There will be no additional solicitations held for third-party evaluation services.
8 | 2023-01-10 | Hello, we just wanted to verify that no official "intent to bid" is due for those who wish to bid on this project. Is that correct? Also, is there a final cut off date for when bidder questions are due? | There is no requirement that bidders notify PSE of an intent to bid. The only requirement is that bidders provide their proposal, in line with requirements stated in the RFP, by March 17, 2023. Bidders can submit any questions regarding the RFP from now until the submission deadline of March 17th.
9 | 2023-01-23 | Can you please provide, or direct me to, the instructions for accessing this site, https://pugetsoundenergy.maps.arcgis.com, referenced as a resource on page 5 of the PSE 2023 Distributed Solar and Storage RFP, Main Document, Section Eligible Resources and Performance Requirements? | Sorry for the confusion. The wrong link was provided and this link [https://pugetsoundenergy.maps.arcgis.com/apps/webappviewer/index.html?id=980fc190ffd648489a492f8363a1d2cc] does not need a PSE account to access. You should be able to freely view the site after reading and agreeing to the terms and conditions that pop-up.
10 | 2023-01-24 | Please send me a link to the PSE Hosting Capacity Heat Map. | See the attached link, [https://pugetsoundenergy.maps.arcgis.com/apps/webappviewer/index.html?id=980fc190ffd648489a492f8363a1d2cc]. You should be able to freely view the site after reading and agreeing to the terms and conditions that pop-up.
11 | 2023-01-24 | My firm is looking forward to submitting our proposals to PSE's RFP. We were hoping to receive some clarity on the specific siting of a potential project. • Can a project be constructed over multiple parcels of land (granted the same landowner / entity owns all the parcels) or must it solely be contained within one parcel? | The Distributed Solar and Storage RFP is currently accepting bids with additional details found in the 2023 DSS RFP section of our website, https://www.pse.com/pages/energy-supply/acquiring-energy. Regarding your question, a project can be constructed over multiple parcels of land, our only concern is that appropriate land rights are captured for each parcel.
12 | 2023-01-26 | Regarding the 200 kW AC minimum size requirement for the 2023 Distributed Solar and Storage RFP, we have two questions regarding aggregation. 1. May we combine separately metered systems, each with less than 200 kW AC of capacity, on separate rooftops but located on contiguous parcels, into a single application in order to meet the minimum threshold? 2. May we physically combine, through trenching and wiring, systems located on separate rooftops each with less than 200 kW AC of capacity, on separate rooftops, into a single application in order to meet the minimum threshold? | Below in red are answers to your question. 1. May we combine separately metered systems, each with less than 200 kW AC of capacity, on separate rooftops but located on contiguous parcels, into a single application in order to meet the minimum threshold? No, a project cannot be separately metered to aggregate to the minimum size of 200 kW AC. 2. May we physically combine, through trenching and wiring, systems located on separate rooftops each with less than 200 kW AC of capacity, on separate rooftops, into a single application in order to meet the minimum threshold? Yes, if the sites are physically combined to meet the minimum threshold that is allowed.
13 | 2023-02-03 | Is there a limit to the PPA terms we are allowed to submit into this bid? | If your question is in regards to contract time length, we will review all terms provided if multiple options are given.
14 | 2023-02-07 | • Does PSE view BESS as a generating asset that would be counted towards available capacity shown on the PSE heat map? For example, if the heat map indicates there is 5MWac of capacity and we are proposing Solar and BESS for the site, would the aggregate capacity limit of both the solar and BESS be 5MWac? • We have multiple sites with access to more than one PSE distribution feeder, does PSE have an interconnection pre-application we can submit which would allow PSE to provide initial guidance on interconnection capacity for distinct sites? • Can PSE add the feeder name to the PSE heat map? • The PSE heat map doesn’t appear to have a layer for identified Non-Wire Alternative (NWA) locations. Please advise how we can identify NWA locations. | • Does PSE view BESS as a generating asset that would be counted towards available capacity shown on the PSE heat map? For example, if the heat map indicates there is 5MWac of capacity and we are proposing Solar and BESS for the site, would the aggregate capacity limit of both the solar and BESS be 5MWac? For a paired project to apply to this RFP, the aggregate capacity must not exceed 4.99 MW AC. For the HCA map, the export of the system should not exceed the value indicated in the HCA layer, otherwise systems improvements will likely be required. • We have multiple sites with access to more than one PSE distribution feeder, does PSE have an interconnection pre-application we can submit which would allow PSE to provide initial guidance on interconnection capacity for distinct sites? There is no interconnection pre-application process, but during the Preliminary Site Assessment and/or Feasibility Study as part of the Schedule 152 process PSE can review alternative routes. • Can PSE add the feeder name to the PSE heat map? Unfortunately PSE is unable to add that extra detail currently to the map. However, during the preliminary site assessment that information can be provided. • The PSE heat map doesn’t appear to have a layer for identified Non-Wire Alternative (NWA) locations. Please advise how we can identify NWA locations. Under the Sumer and Winter Substation Loading Forecast layer, there is a qualifier titled “NWA Eligible” when you click on any colored region. Some of the highly loaded regions will have a YES acknowledgement to them. There is also a Group Filter you can do just for NWA Eligible.
15 | 2023-02-10 | As part of the RFP response, PSE requires the bidder to submit “Preliminary Site Assessment Requests” with the interconnection team for these projects. Therefore, we were hoping to request a sample “Pre-application form” and minimum data requirements related to the project as needed for the preliminary assessment. We have logged into Power Clerk. However, we couldn’t identify an option to submit pre-application via this portal. We have also reviewed PSE’s Generator Overview of Schedule 152 Interconnection Process in preparation for the official interconnection applications and scoping meeting with PSE team. | To submit a proposal for the RFP, you don’t have to submit an application for the Preliminary Site Assessment. By filling out Exhibit B of the DSS RFP and paying the study fee, you will provide our team with everything required for the preliminary assessment. However by May 19th a full Schedule 152 application will need to have been submitted.
16 | 2023-02-13 | 1. Will PSE be metering at 480v or distribution voltage (13 kV)? 2. Who owns the transformer? 3. Will PSE require separate service/meter between BESS/Solar if both are on one parcel or can both technologies be behind a common meter? 4. On page 3 of the RFP, it states “BESS paired with solar must not exceed the nameplate value of the solar facility”. However, in your response below PSE indicated that “For a paired project to apply to this RFP, the aggregate capacity must not exceed 4.99 MW AC.” a. Can the size of the BESS system for a paired system exceed the AC capacity of the PV system? | 1. Will PSE be metering at 480v or distribution voltage (13 kV)? If the project has an aggregated capacity of 4-5MWs then PSE will be metering at distribution voltage, primary service. However, this answer can change pending study results. 2. Who owns the transformer? If the facility takes primary service (12/13 kV), the customer will purchase and own the transformer. However, this answer can change pending study results. 3. Will PSE require separate service/meter between BESS/Solar if both are on one parcel or can both technologies be behind a common meter? There is no set rule on how the metering should be configured. Both can be behind a common meter. 4. On page 3 of the RFP, it states “BESS paired with solar must not exceed the nameplate value of the solar facility”. However, in your response below PSE indicated that “For a paired project to apply to this RFP, the aggregate capacity must not exceed 4.99 MW AC.” a. Can the size of the BESS system for a paired system exceed the AC capacity of the PV system? The BESS system AC capacity cannot exceed the PV system. In the case of maximizing MWs equally on a paired system, the PV system will be limited to 2.495 MWs and the BESS 2.495 MWs. The aggregate capacity cannot exceed 4.99 MWs AC.
17 | 2023-02-14 | We have the below questions on the RFP requirements for the 2023 DSS RFP 1. (a) Is the 5 MWac project size limit per legal parcel? For example, can we submit two different 3 MWac projects on a single legal parcel if they’re located on two distinct areas of the site and we have confidence the feeder lines have capacity for the combined power? Or would we have to subdivide the site? (b) Tab 3 in Exhibit B of the RFP speaks to projects which have the ability to be expanded upon. Is this only up to 5 MWac or shall we also indicate projects which can be expanded upon, greater than 5 MWac? 2. In Exhibit B, Section 4: Proposal Requirements, Proposal Requirement 1.01 states that the respondent must provide CETA compliant resource(s). Does this requirement just speak to answering “yes” to the questions that are listed under the Customer Benefits from Transition to Clean Energy Plan in Exhibit B, Section 2a: Commercial Details? In other words, must the proposed resource comply with any CETA requirements beyond those described in Section 2a in order for the respondent to be able to select “Comply?” | 1. (a) Is the 5 MWac project size limit per legal parcel? For example, can we submit two different 3 MWac projects on a single legal parcel if they’re located on two distinct areas of the site and we have confidence the feeder lines have capacity for the combined power? Or would we have to subdivide the site? The project size is not limited by the land parcel. Two projects can be sited on a single parcel, but a detailed study will need to be completed for each project to determine system impacts and potential system upgrades. The two projects will have to be separately metered with two points of interconnection. (b) Tab 3 in Exhibit B of the RFP speaks to projects which have the ability to be expanded upon. Is this only up to 5 MWac or shall we also indicate projects which can be expanded upon, greater than 5 MWac? For this RFP the capacity is capped up to 4.99 MW AC for a project, but we are curious if your project can be expanded. Any expansion would have to occur in a later phase outside of this solicitation, but understanding the future potential is useful. 2. In Exhibit B, Section 4: Proposal Requirements, Proposal Requirement 1.01 states that the respondent must provide CETA compliant resource(s). Does this requirement just speak to answering “yes” to the questions that are listed under the Customer Benefits from Transition to Clean Energy Plan in Exhibit B, Section 2a: Commercial Details? In other words, must the proposed resource comply with any CETA requirements beyond those described in Section 2a in order for the respondent to be able to select “Comply?” For Exhibit B, Section 4: Proposal Requirements, requirement 1.01 is meant as an acknowledgment from the bidder that their project is a renewable resource that helps PSE meet its requirements outlined in RCW 19.405.040 and defined in RCW 19.405.020. There are additional items in the Customer Benefits from Transition to Clean Energy Plan in Section 2a that step outside of the scope of CETA compliancy. In essence 1.01 is just asking if your project is considered a renewable resource as defined by CETA.
18 | 2023-02-16 | Thank you for the link to the HC map, it is very useful. For proper use, I would need some clarifications on the information available. Could you please confirm that the Hosting capacity value displayed: • takes into account the ampacity of the cable, • does Not take into account : o the voltage screen (voltage drop and rise), o the anti-islanding limit, o the protection upgrades (feeder and substation), o and the other projects on the queue. Is there a way to know the substation’s location and the line’s voltage level? If not, is it correct to assume most of the lines are 12.47kV? I understand that even if a project is under the [Hosting Capacity], the screens not taken into account could generate additional costs (regulators, 3V0 substation upgrade, direct transfer trip, etc…). Is that correct? | The hosting capacity map includes both loading and power quality limitations, including: • Equipment loading • Reverse power flow • Under/Over Voltage • Voltage deviation It does not include anti-islanding, protection upgrades, or other projects on the queue. Is there a way to know the substation’s location and the line’s voltage level? If not, is it correct to assume most of the lines are 12.47kV? No, the substation’s location cannot be provided for security purposes and the line voltage is not provided in the map. The vast majority of PSE’s distribution system is 12.47kV, with some targeted areas operating at 34.5 kV. I understand that even if a project is under the [Hosting Capacity], the screens not taken into account could generate additional costs (regulators, 3V0 substation upgrade, direct transfer trip, etc…). Is that correct? Yes, through the study process additional equipment and upgrades might be identified that could add to the project cost.
19
20
21
22
23
24
25
26
27