## Requirements
Number | Functional Area | Capability | Aggregator | Direct Connect | Requirement | Must Have | Nice to Have | Future
1.01 | Business | Customer | ü |  | Respondent must have a customer consent and authorization process. |  | ü
1.02 | Business | Customer | ü |  | Respondent shall specify how event notification will be sent to PSE customers | ü
1.03 | Business | Co-branding | ü |  | Respondent must use PSE branding or co-branding when sending notifications to customers for programs with the potential for PSE ownership. For programs that will not be owned by PSE, PSE branding or co-branding is preferred, but if that option is not technically possible please explain alternative. | ü
1.04 | Business | DER Types | ü | ü | Respondent must provide CETA compliant resource(s) | ü
1.05 | Business | DER Types | ü |  | Respondent is requested to be able to leverage different DER sub-types to meet commitments. For example, if a Respondent is intending to aggregate batteries PSE requests the Respondent be able to interface with different types of batteries (ex. Tesla, Generac, etc) |  | ü
1.06 | Business | Performance | ü | ü | Respondents proposing dispatchable resources must provide detailed event performance measurements and perform M&V. Respondent shall specify what M&V and baseline capabilities they have. | ü
1.07 | Business | Performance | ü | ü | Respondent must acknowledge that PSE may implement financial penalties for non-performance of kW / kWh targets | ü
1.08 | Business | Planned outage | ü | ü | Respondent must provide PSE 7 days advanced notice for any planned DER outage | ü
1.09 | Business | Planned outage | ü | ü | Respondent must provide 7 days advanced notice for any DER testing | ü
1.1 | Business | Record maintenance | ü |  | Respondent must have a protocol for managing customer consent, including for how long verifiable proof of consent is retained. |  | ü
1.11 | Business | Record maintenance | ü |  | Respondent must have a protocol for managing shared customer information. Ex if a customer leaves the aggregator, how long will their customer information be retained in the aggregator's system. | ü
1.12 | Business | Record maintenance | ü |  | Respondent must allow customers to be able to revoke authorization/consent and withdraw from participation | ü
1.13 | Business | Compliance | ü | ü | Respondent must comply with all applicable laws and regulations. Respondent must ensure that all proposed resources comply with all applicable PSE, WA state, and national safety standards. As applicable, respondent must support PSE's compliance with privacy laws and regulations including WAC 480-100-153 and WAC 480-90-153. | ü
1.14 | Business | Sale of information | ü |  | Respondent must not sell any customer information obtained from PSE or from the customer through PSE programs | ü
1.15 | Business | Settlement | ü | ü | Respondent must support settlement process with both DER owners and PSE | ü
2.01 | Engineering | Asset Management | ü | ü | Respondent must provide the physical location of the DER resource allowing PSE to match it with the distribution feeder it is connected to. It is assumed and expected that the vendor/supplier of the project will provide the GIS data to PSE in electronic form to be consumed or entered into our SAP CIS, GIS, Virtual Power Plant, and SCADA EMS systems. | ü
2.02 | Engineering | Asset Management | ü | ü | Respondent must provide DER nameplate, resource availability, response information to PSE. This information needs to be provided at individual DER level for DER > 25kVa and aggregated (at least down to feeder level) for smaller resources. | ü
2.03 | Engineering | Asset Management | ü | ü | Respondent must provide PSE with the ability to send dispatch and control commands to individual DERs > 25 kVa and to geographically aggregated resources (at least down to feeder level) for smaller resources | ü
2.04 | Engineering | Communications | ü | ü | Respondent requested to be capable of communicating using the following: -Standards and protocols: IEEE 2030.5, DNP3 SCADA protocol devices, Modbus SCADA protocol devices, SunSpec Smart Inverter Profile (Modbus or DNP3), MESA Storage Profile (Modbus or DNP3), ICCP -Networks: AMI, LTE cellular, Broadband Respondent requested to describe experience with: -IEEE 2030.5: Describe communications experience with IEEE 2030.5 and specify equipments (i.e. battery controller, inverter, etc) controlled by the IEEE signal -LTE Cellular: What cellular carrier is being proposed and what carriers have you used in the past? Where was this done? | ü
2.05 | Engineering | Communications |  | ü | Respondent requested to validate that the DER can communicate through LTE cellular or fiber connections using real-time data with IEEE 2030.5 or DNP 3.0 communication standards . Supplier to specify which cellular carrier is being proposed? Please provide what cellular carriers have you used in the past? Where was this done? What PCS (Power Control System) and Inverter equipment did you communicate with (i.e., battery controller, inverter, both) ? Were Watch Dog Timers and diagnostics used if communication failures occured? | ü
2.06 | Engineering | Grid Operation | ü | ü | Respondent must adhere to all applicable PSE interconnection processes, comply with all applicable PSE technical specifications and open industry communication standards, including the interconnection requirements set forth in: -PSE's Tariff Schedule 152 - Interconnection with Electric Generators (https://www.pse.com/-/media/Project/PSE/Portal/Rate-documents/Electric/elec_sch_152.pdf) -IEEE 1547-2018: Standard for Interconnection and Interoperatbility of Distributed Energy Resources with Associated Electric Power System Interfaces (https://standards.ieee.org/products-services/standards-related/pdf/electric-power-systems.html), and -PSE's Technical Specification and Operating Procedures for Interconnection of Generation Facilities Not Subject to FERC Jurisdiction (https://www.oasis.oati.com/woa/docs/PSEI/PSEIdocs/PSE-ET-160.70_NonFERC_19Aug07.pdf) | ü
2.07 | Engineering | Inverter | ü | ü | Respondent must provide DER inverter specifications to PSE including, but not limited to: -Rated AC output power, current, and voltage; -Power factor range of adjustability; -Available voltage and frequency protective elements; -Available grid support functions (anti-islanding, voltage ride through, voltage support, etc.); -Available communication protocols; -Grid standard (IEEE 1547 and UL1741) compliance information | ü
3.01 | IT | Compliance | ü |  | Respondent must be certified and include proof of a current SOC2 audit for SaaS and Cloud software implementations. On premise Respondents do not need an SOC2 audit. Respondents who are in the process of a SOC2 audit will be considered if a letter is provided from their auditor stating they are in a SOC2 audit and have an estimated completion date by July 1, 2022. | ü
3.02 | IT | Cybersecurity | ü |  | Respondent must meet industry best practices for security standards set by NIST-IR 7628 | ü
3.03 | IT | Cybersecurity | ü |  | Respondent must encrypt data in motion using TLS 1.2+ | ü
3.04 | IT | Cybersecurity | ü |  | Respondent must encrypt data at rest using AES-256 or better | ü
3.05 | IT | Cybersecurity | ü |  | Respondent must support standard approaches for network connectivity to the Respondent platform, including firewall rules on both sides, IP restrictions to PSE’s external IP range, and VPN connectivity for connections back to PSE OT systems, amongst others. Details will be determined during the design phase of the implementation project | ü
3.06 | IT | Cybersecurity | ü |  | Respondent shall provide cyber security features, including but not limited to: authentication, encryption, access control, event and communication logging, monitoring and alarming to protect the system from unauthorized modification or use | ü
3.07 | IT | Cybersecurity | ü |  | Respondent shall verify that the addition of security features does not adversely affect connectivity, latency, bandwidth, response time and through-put (including during the Site Acceptance Testing (SAT) when connected to existing equipment) | ü
3.08 | IT | Cybersecurity | ü | ü | Respondent shall remove or disable all software components that are not required for the operation and maintenance of the device prior to the Factory Acceptance Testing (FAT). The Respondent shall provide documentation on what is removed and/or disabled | ü
3.09 | IT | Cybersecurity | ü | ü | Respondent shall provide, within a pre-negotiated period, appropriate software and service updates and/or workarounds to mitigate all vulnerabilities associated with the product and to maintain the established level of system security | ü
3.1 | IT | Cybersecurity | ü | ü | Respondent shall certify that its systems and products have undergone cyber security testing by leading and independent government sanctioned organizations | ü
3.11 | IT | Cybersecurity | ü | ü | After contract award, the Respondent shall provide notification of known security vulnerabilities affecting the Respondent supplied or required operating system, application and critical third-party software within a pre-negotiated period after public disclosure | ü
3.12 | IT | Cybersecurity | ü | ü | After contract award, the Respondent shall provide notification of a patch(es) affecting security within a pre-negotiated period, as identified in the patch management process. The Respondent shall apply, test and validate the appropriate updates and/or workarounds on a baseline reference system before distribution. Mitigation of these vulnerabilities shall occur within a pre-negotiated period | ü
3.13 | IT | Cybersecurity | ü |  | After contract award, the Respondent shall provide firewalls and firewall rule sets between network zones or provide firewall rule sets if the firewalls are not provided by the Respondent. The Respondent shall provide firewall rule sets and/or other equivalent documentation. The basis of the rule set shall be “deny all,” with exceptions explicitly identified by the Respondent. Note that this information is deemed business sensitive and shall be protected as such | ü
3.14 | IT | Cybersecurity | ü |  | After contract award, the Respondent shall provide detailed information on all communications (including protocols) required through a firewall, whether inbound or outbound, and identify each network device initiating a communication in accordance with the corresponding rule sets | ü
3.15 | IT | Cybersecurity | ü |  | Respondent shall not permit user credentials to be transmitted in clear text. The Respondent shall provide the strongest encryption method commensurate with the technology platform and response time constraints. The Respondent shall not allow applications to retain login information between sessions, provide any auto-fill functionality during login or allow anonymous logins. The Respondent shall provide user account-based logout and timeout settings | ü
3.16 | IT | Cybersecurity | ü |  | Respondent shall provide a configurable account password management system that allows for selection of password length, frequency of change, setting of required password complexity, number of login attempts, inactive session logout and denial of repeated or recycled use of the same password | ü
3.17 | IT | Cybersecurity | ü |  | Respondent shall not store passwords electronically or in Respondent-supplied hardcopy documentation in clear text unless the media is physically protected. The Respondent shall control configuration interface access to the account management system. The Respondent shall provide a mechanism for rollback of security authentication policies during emergency system recovery or other abnormal operations where system availability would be negatively impacted by normal security procedures | ü
3.18 | IT | Cybersecurity | ü |  | Respondent shall provide a system whereby account activity is logged and is auditable both from a management (policy) and operational (account use activity) perspective. The Respondent shall time stamp and control access to audit trails and log files. The Respondent shall ensure audit logging does not adversely impact system performance requirements | ü
3.19 | IT | Cybersecurity | ü |  | Respondent shall provide for user accounts with configurable access and permissions associated with the defined user role. The Respondent shall adhere to least privileged permission schemes for all user accounts and application-to-application communications | ü
3.2 | IT | Cybersecurity | ü |  | Respondent shall verify that a user cannot escalate privileges, under any circumstances, without logging into a higher-privileged role first. The Respondent shall provide a mechanism for changing user(s) role (e.g. group) associations. After contract award, the Respondent shall provide documentation defining access and security permissions, user accounts, applications and communication paths with associated roles | ü
3.21 | IT | Cybersecurity | ü |  | Respondent shall provide a Single Sign-On (SSO) such that Role-based Access Control (RBAC) enforcement is equivalent to that enforced as a result of direct login. This system should be RBAC capable. The Respondent shall provide documentation on configuring such a system and documentation showing equivalent results in running validation tests against the direct login and the SSO. The Respondent shall protect key files and Access Control Lists (ACLs) used by the SSO system from non-administrative user read, write and delete access. Note that SSO must resolve individual user’s logins to each application | ü
3.22 | IT | Cybersecurity | ü |  | The Respondent shall have and provide documentation of a written flaw remediation process for all software they develop. The Respondent shall provide appropriate software updates and/or workarounds to mitigate all vulnerabilities associated with the flaw within a pre-negotiated period. | ü
3.23 | IT | Cybersecurity | ü |  | After contract award, when the Respondent is made aware of or discovers any flaws, the Respondent shall provide notification of such flaws affecting security of Respondent-supplied software within a pre-negotiated period. Notification shall include, but is not limited to, detailed documentation describing the flaw with security impact, root cause, corrective actions, etc. (This language is typically found in a quality assurance document, but is included here for completeness.) | ü
3.24 | IT | Cybersecurity | ü |  | Respondent's aggregation system must track and maintain third-party penetration tests | ü
3.25 | IT | Cybersecurity | ü |  | Respondent's aggregation system must log all events, including security-related event status with an accurate timestamp. | ü
3.26 | IT | Cybersecurity | ü |  | Respondent's aggregation system must not require read/write/execute access to filesystems outside its web root folder and must not execute OS-level commands based off of user input | ü
3.27 | IT | Cybersecurity | ü |  | Respondent's aggregation system must physically or logically separate PSE’s data from other of Respondent’s customers’ data | ü
3.28 | IT | Cybersecurity | ü |  | Respondent's aggregation system must secure API access and system connectivity (e.g., API keys, SSH keys) | ü
3.29 | IT | Cybersecurity | ü |  | Respondent's aggregation system must support single sign-on using SAML 2.0. | ü
3.3 | IT | Data security | ü | ü | Respondent must comply with PSE's Security Addendum (Consultant or Hosted) and ensure data security for all relevant usage, metering, settlement, and customer information. | ü
3.31 | IT | Data security | ü |  | Respondent must secure customer data and describe the manner in which this data is secured. | ü
3.32 | IT | Deployment | ü |  | Respondent to indicate preferred pattern of solution. PSE's preference is for SaaS solution, but will consider other deployment patterns. If not SaaS, please provide details on architecture. |  | ü
3.33 | IT | High Availability | ü |  | Respondent must support a high-availability architecture. Please describe your product's architecture to support a high level of reliability. What is your committed level of product up-time? Is your VEN system capable of meeting a 99.9% availability SLA ? | ü
3.34 | IT | High Availability | ü |  | Respondent shall support high availability operations with redundant infrastructure and communications along with continuous automated monitoring, alerting and automated failover | ü
3.35 | IT | Integration | ü |  | Respondent must have the ability to interface with and be controlled by the PSE VPP. Respondent must support reliable connections to SaaS and cloud-hosted software and support a programmatic interface to the PSE VPP implementation. Please describe best practices for integration of your software to the PSE VPP. | ü
3.36 | IT | Integration | ü |  | Respondent must be able to integrate DER monitoring, control, and dispatch to PSE VPP using Open ADR 2.0b | ü
3.37 | IT | Integration | ü | ü | For VPP interfacing resources, Respondent is requested to provide a list of presently operational VPP interfaces and a separate list of VPP interfaces that have only been piloted. | ü
3.38 | IT | Offshore | ü |  | Respondent must use datacenters located in the US for SaaS or Cloud | ü
3.39 | IT | Standards | ü |  | Supplier / Respondent shall be requested that their DER system has the capability to be configured as a OpenADR VEN. PSE's VPP shall act as the VTN Gateway as defined in the OpenADR 2.0b specification. PSE requires to have two way real time data communication between the VPP and Aggregrator plaftorm using OpenADR 2.0b. |  | ü
3.4 | IT | Standards | ü | ü | Respondent requested that system be capable of fully complying with and capable of communicating to DER (BESS or PV storage system) using a smart inverter with its PCS system. PSE requires that the Smart Inverter incorporate or embed into its controls the SunSpec interoperability standards. These standards and communication protocols shall be as follows: * IEEE 2030.5 * DNP3.0 * Modbus TCP The above communication protocols shall provide open interoperability and real-time communication to the PCS control system and components which the Smart Inverter is part of the controls equipment. Security with the Smart Inverter shall also include: PSE security requirements, TLS, PKI infrastructure, Digital Certificates and authority, encryption (SHA-256), authenication, authorization, indentities, and client identification with the above communications. The Sunspec Standard shall provide a DER and Device Information Data Model to collect, read, and write data to the Smart Inverter. This shall consist of CSIP profile for the inveter, monitoring power production data (kWH, kW, Delivered, Received, charging ramp rates, alarms, chargeing schedules, events, over/under voltage, over/under current, Frequeny, and all power-voltage imbalances). It shall also provide connect and disconnect functions, High/low voltage ride through, Volt-Var, and PF control functions. PSE requires reporting data capabilities as well with Real and Reactive Power, Volts, Amps, Hz, and PF for all 3 phases + Neutral including Averages. |  | ü
3.41 | IT | Standards | ü |  | Respondent is requested to have the capability to be dispatched via open standards or non-proprietary protocols. Please describe preferred and outline any other feasible mechanisms for dispatch of DER assets. |  | ü
3.42 | IT | Standards | ü | ü | Supplier/Respondent must have the ability with their PCS system (Power Control System) to have rate schedules managed by the VPP. The expectation is that system supports both direct and indirect control with rate and charging schedules. This can be managed by an Aggregrator using open protocols such as IEEE-2030.5 or DNP 3.0 but must coordinate and integrate with the VPP via OpenADR 2.0b as a VEN. If direct control is use by PSE VPP/DERMS system then the supplier shall support PSE standards of IT/OT communications direct to the energy storage controller. | ü
4.01 | Load Office | DER Control |  | ü | Respondent must have the ability to be managed by, interface with, and directly be controlled by the PSE VPP for solar deployments >=0.5MW and <2MW and FOTM BESS <2MW | ü
4.02 | Load Office | Dispatch | ü | ü | Supplier/Respondent must have the capability with its DER site controls, communication to aggregrators and VPP to indicate resource availability, readiness, and equipment states of all components at the DER to dispatch the DER resource. | ü
4.03 | Load Office | Forecasting | ü | ü | Respondent required to have the capability to provide generation capacity up to 48 hours in advance | ü
4.04 | Load Office | Forecasting | ü | ü | Respondent requested to have the capability to provide generation capacity up to 7 days in advance |  | ü
4.05 | Load Office | Price | ü |  | Respondent must provide price of dispatch with generation forecast | ü
5.01 | Operations | Alarms | ü | ü | The Supplier/Respondent shall have the ability to provide DER controls which manage all states, alarms and events to the VPP. This shall include watch dog timers for communication, loss of end-points or loss of phyiscal or communication to the site. If the communications is lost the communications shall retry to establish communications. If communications is lost an alert and alarm shall occur. All states and events shall also be managed so that root cause analysis can be determined to what caused the failure. |  | ü
5.02 | Operations | Control | ü |  | Respondent must have the ability to be enabled and disabled by the VPP | ü
5.03 | Operations | Control | ü | ü | Supplier/ Respondent shall have the capability to respond to real time control from the VPP (source) to the DER PCS controls (site). Communications shall have the ability to perform read request, respond and write data including all PCS configuration controller data. |  | ü
5.04 | Operations | Control | ü | ü | Supplier/Respondent must be capable of enabling control of the DER site from the VPP. The interval between control command request and response back to the VPP should be less than 15 seconds. PSE ultimately desires to have 5 second or better response time from request from the VPP to response from the DER. | ü
5.05 | Operations | Data interval | ü | ü | Supplier/Respondent must be capable of enabling processes for the DER site to be managed from the VPP for all data collection with DER Asset Production Resource data. PSE desires to have 15 second response time from a read request and write from the VPP to the DER. PSE ultimately desires to have 5 second or better response time from read request from the VPP to response from the DER. | ü
5.06 | Operations | Event response | ü | ü | Respondent's time window for providing full capacity for a dispatched event, which PSE notifies an hour ahead, is how large (within a minute, five mins, etc…)? | ü
5.07 | Operations | Event response | ü | ü | Respondent must be able to provide confirmation of opt-out of events to the VPP | ü
5.08 | Operations | Event response | ü | ü | Respondent must be able to receive event notifications from the VPP | ü
5.09 | Operations | Event response | ü | ü | Respondent must be able to respond to day-ahead events. Respondent shall describe their notification requirements in order to successfully respond to an event, including minimum advanced notice time interval. | ü
5.1 | Operations | Event response | ü | ü | Respondent requested to have the capability to respond to hour-ahead events |  | ü
5.11 | Operations | Ride-through |  | ü | Respondent must ensure that inverters ride-through momentary outages according to standard IEEE 1547 -2018, standard CA-21, and standard UL-1741. | ü
5.13 | Operations | SCADA |  | ü | Respondent is required, for direct connect DER, to provide interconnection architecture (building upon included diagrams and including more detail) that shows the connectivity with meter, DER, utility service point, transformer highlighting the energy flow, and the communication standards used to communicate between the devices. | ü
5.14 | Operations | SCADA | ü |  | Respondent is required, for Aggregated DER, to provide interconnection architecture (building upon included diagrams and including more detail) that shows the connectivity with meter, DER, utility service point, transformer highlighting the energy flow, and the communication standards used to communicate between the devices. Additionally, Respondent is requested to provide integration mechanism and cybersecurity controls around integration to the PSE VPP. | ü
5.15 | Operations | SCADA |  | ü | Respondent must provide a persistent connection to DER for monitoring, control, and metering purposes to the PSE SCADA system for DER > 25 kVA | ü
5.16 | Operations | SCADA |  | ü | Respondent requested to provide communication status of the DER monitoring, control, dispatch link to the VPP |  | ü
5.17 | Operations | SCADA |  | ü | Respondent must be able to curtail DER when instructed by PSE for DER > 25kVA | ü
5.18 | Operations | SCADA |  | ü | Respondent is requested to provide digital and analog points for SCADA connected DER > 25 kVA |  | ü
5.19 | Operations | VPP | ü | ü | Respondent requested to provide DER status, performance, and configuration data to the VPP |  | ü
5.2 | Operations | VPP | ü |  | Respondent shall have the capability to dispatch an event if communication is lost to VPP | ü
5.21 | Operations | VPP | ü |  | Respondent shall have the capability to issue acknowledgement signals to VPP indicating a certain command or request has been received | ü
5.22 | Operations | VPP | ü |  | Respondent shall specificy their methodology for handling multiple events or how different DERs will be bid for a specific program |  |  | ü
5.23 | Operations | Maintenance | ü | ü | For any response with a PSE ownership option, Respondent shall provide equipment maintenance requirements | ü
6.01 | Planning | Forecast | ü | ü | Respondent shall provide to PSE annually updated 8760 DER forecast and normative load shapes for DERs >=500kVA. | ü
6.02 | Planning | Forecast | ü |  | Respondent requested to provide regression-based DER growth models for 2 year time period |  | ü
6.03 | Planning | Forecast | ü |  | Respondent requested to provide a time-based DER growth and availability model for 2 years |  | ü