## Readme
This workbook provides a summary of each of the Generic Resource costs extracted from technical sources documented in the 2021 National Renewable Energy Laboratory (NREL) Annual Technology Baseline (ATB) cost report which are relevant to options to be considered in the 2023 Electric Progress Report portfolio planning process and details of how PSE has adjusted those costs to come to finalized Generic Resource costs for use in the 2023 Electric Progress Report.
Objective
The objective of this document is to provide a detailed look at the breakdown of capital costs of Generic Resources and adjustments made to those costs that reflect assumptions that PSE has made based on information available from operating characteristics and internal sources of information. Costs provided may differ from the actual costs modeled in the 2023 Electric Progress Report as new information is available and assumptions are updated.
Definitions
| Capital Cost | This document presents the CAPEX or total capital expenditure required to achieve commerical operation of the generation plant, as published in the 2021 NREL ATB. The 2021 NREL ATB does not provide an in-depth review of the numerous components which compose the total capital cost of a generating resource. Therefore, PSE has reviewed the source materials cited in the 2021 NREL ATB to get an understanding of the components of each technology's capital cost, for example: equipment costs, balance of plant costs and financing costs. Often times, the total capital costs of the source materials differed from the costs presented in the NREL ATB. In these cases, PSE used the ratio of the total capital cost of the source materials to the total capital cost of the NREL ATB to scale component costs to gain an understanding of the contribution of each component to the NREL ATB cost. In cases, where PSE deemed it necessary to make an adjustment to the capital cost of a resource, the cost is applied to the specific component which required an adjustment.
Other Notes:
Dollar values are in 2020 US Dollars, unless otherwise noted.
Reference:
2021 National Renewable Energy Laboratory Annual Technology Baseline: https://atb.nrel.gov/electricity/2021/data
Please refer to companion workbook on NREL ATB Cost Breakdown for complete listing of data sources.

## Cost Curves
Cost curves across all available resources, all listings in 2020 dollars per kiloWatt
Year | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
Offshore Wind | 5315.5952 | 4972.1452 | 4715.9175 | 4507.4827 | 4329.2779 | 4171.9346 | 4029.8606 | 3899.4488 | 3778.2363 | 3664.4664 | 3556.842 | 3454.3781 | 3399.4987 | 3348.4072 | 3300.6142 | 3255.7197 | 3213.392 | 3173.3534 | 3135.369 | 3099.2382 | 3064.7886 | 3031.8706 | 3000.3538 | 2970.1237 | 2941.0795 | 2913.1315 | 2886.2 | 2860.2137 | 2835.1085 | 2810.8266 | 2787.3156 | 2764.5281
Onshore Wind | 1484.4 | 1438.729 | 1393.0581 | 1347.3871 | 1301.7162 | 1256.0452 | 1210.3743 | 1164.7033 | 1119.0324 | 1073.3614 | 1027.6905 | 982.0195 | 972.1993 | 962.3791 | 952.5589 | 942.7387 | 932.9185 | 923.0983 | 913.2781 | 903.4579 | 893.6377 | 883.8175 | 873.9974 | 864.1772 | 854.357 | 844.5368 | 834.7166 | 824.8964 | 815.0762 | 805.256 | 795.4358 | 785.6156
Solar_Utility | 1429.6696 | 1414.6458 | 1352.9201 | 1291.1945 | 1229.4689 | 1167.7433 | 1106.0176 | 1044.292 | 982.5664 | 920.8408 | 859.1151 | 797.3895 | 790.2841 | 783.1787 | 776.0732 | 768.9678 | 761.8624 | 754.757 | 747.6515 | 740.5461 | 733.4407 | 726.3353 | 719.2299 | 712.1244 | 705.019 | 697.9136 | 690.8082 | 683.7027 | 676.5973 | 669.4919 | 662.3865 | 655.281
Solar_Residential | 2842.6772 | 2777.8922 | 2603.021 | 2428.1498 | 2253.2786 | 2078.4075 | 1903.5363 | 1728.6651 | 1553.7939 | 1378.9228 | 1204.0516 | 1029.1804 | 1017.7716 | 1006.3628 | 994.9539 | 983.5451 | 972.1363 | 960.7275 | 949.3187 | 937.9098 | 926.501 | 915.0922 | 903.6834 | 892.2745 | 880.8657 | 869.4569 | 858.0481 | 846.6392 | 835.2304 | 823.8216 | 812.4128 | 801.004
Battery, LI 2hr | 986.3231 | 936.1386 | 882.2395 | 828.3405 | 774.4415 | 720.5425 | 666.6435 | 646.6896 | 626.7357 | 606.7817 | 586.8278 | 566.8739 | 560.764 | 554.654 | 548.5441 | 542.4342 | 536.3243 | 530.2143 | 524.1044 | 517.9945 | 511.8845 | 505.7746 | 499.6647 | 493.5547 | 487.4448 | 481.3349 | 475.225 | 469.115 | 463.0051 | 456.8952 | 450.7852 | 444.6753
Battery, LI 4hr | 1633.9238 | 1553.0397 | 1460.2286 | 1367.4175 | 1274.6063 | 1181.7952 | 1088.984 | 1049.8336 | 1010.6832 | 971.5327 | 932.3823 | 893.2318 | 882.0664 | 870.901 | 859.7356 | 848.5702 | 837.4048 | 826.2394 | 815.074 | 803.9086 | 792.7432 | 781.5779 | 770.4125 | 759.2471 | 748.0817 | 736.9163 | 725.7509 | 714.5855 | 703.4201 | 692.2547 | 681.0893 | 669.9239
Battery, LI 6hr | 2285.6073 | 2173.7965 | 2041.8807 | 1909.965 | 1778.0493 | 1646.1336 | 1514.2178 | 1455.8413 | 1397.4648 | 1339.0883 | 1280.7117 | 1222.3352 | 1206.0981 | 1189.8611 | 1173.624 | 1157.3869 | 1141.1498 | 1124.9128 | 1108.6757 | 1092.4386 | 1076.2015 | 1059.9645 | 1043.7274 | 1027.4903 | 1011.2532 | 995.0162 | 978.7791 | 962.542 | 946.3049 | 930.0679 | 913.8308 | 897.5937
Battery, Residential | 4578.7891 | 4318.5755 | 4082.5909 | 3846.2094 | 3631.6263 | 3434.2594 | 3250.4559 | 3147.1414 | 3054.7966 | 2974.205 | 2895.7063 | 2824.3925 | 2789.0876 | 2753.7827 | 2718.4778 | 2683.1729 | 2647.868 | 2612.5631 | 2577.2581 | 2541.9532 | 2506.6483 | 2471.3434 | 2436.0385 | 2400.7336 | 2365.4287 | 2330.1238 | 2294.8189 | 2259.514 | 2224.2091 | 2188.9042 | 2153.5993 | 2118.2944
Solar + Battery | 1354.868 | 1320.8784 | 1255.4793 | 1190.0803 | 1124.6812 | 1059.2822 | 993.8832 | 945.1195 | 896.3558 | 847.5921 | 798.8284 | 750.0647 | 742.3871 | 734.7095 | 727.0319 | 719.3543 | 711.6767 | 703.9991 | 696.3215 | 688.6439 | 680.9663 | 673.2888 | 665.6112 | 657.9336 | 650.256 | 642.5784 | 634.9008 | 627.2232 | 619.5456 | 611.868 | 604.1904 | 596.5129
Wind + Battery | 1408.2572 | 1355.4387 | 1298.9228 | 1242.4068 | 1185.8908 | 1129.3748 | 1072.8588 | 1032.9782 | 993.0975 | 953.2169 | 913.3363 | 873.4556 | 864.0288 | 854.6019 | 845.1751 | 835.7483 | 826.3215 | 816.8946 | 807.4678 | 798.041 | 788.6141 | 779.1873 | 769.7605 | 760.3336 | 750.9068 | 741.48 | 732.0531 | 722.6263 | 713.1995 | 703.7726 | 694.3458 | 684.919
Wind + Solar + Battery | 1692.4448 | 1646.1448 | 1576.2878 | 1506.4308 | 1436.5738 | 1366.7168 | 1296.8598 | 1239.4793 | 1182.0988 | 1124.7183 | 1067.3378 | 1009.9573 | 999.725 | 989.4928 | 979.2605 | 969.0282 | 958.7959 | 948.5636 | 938.3313 | 928.0991 | 917.8668 | 907.6345 | 897.4022 | 887.1699 | 876.9377 | 866.7054 | 856.4731 | 846.2408 | 836.0085 | 825.7763 | 815.544 | 805.3117
CCCT | 1083.7987 | 1079.2875 | 1073.6486 | 1071.3931 | 1058.9875 | 1054.4763 | 1054.4763 | 1049.9652 | 1040.9429 | 1036.4318 | 1031.9207 | 1027.4096 | 1024.0262 | 1019.5151 | 1012.7484 | 1009.365 | 1004.8539 | 999.215 | 994.7039 | 991.3205 | 986.8094 | 982.2983 | 977.7871 | 973.276 | 969.8927 | 965.3815 | 961.9982 | 958.6148 | 954.1037 | 948.4648 | 943.9537 | 932.6758
Frame Peaker | 1035.4721 | 1025.7721 | 1016.0721 | 1011.2221 | 990.6097 | 979.6972 | 976.0597 | 968.7848 | 954.2348 | 946.9598 | 940.8973 | 936.0474 | 932.4099 | 926.3474 | 920.2849 | 915.4349 | 910.5849 | 904.5224 | 899.6725 | 894.8225 | 891.185 | 885.1225 | 880.2725 | 875.4225 | 870.5725 | 865.7226 | 862.0851 | 857.2351 | 852.3851 | 847.5351 | 841.4726 | 831.7726
Biomass | 4504.599 | 4490.829 | 4477.0589 | 4463.0689 | 4433.6511 | 4431.2172 | 4431.1654 | 4408.2087 | 4386.239 | 4362.915 | 4337.5608 | 4307.9981 | 4283.3651 | 4250.9683 | 4216.3394 | 4187.4632 | 4158.2031 | 4126.4384 | 4096.8015 | 4068.663 | 4041.9443 | 4012.5412 | 3980.3345 | 3952.7278 | 3925.7506 | 3898.484 | 3874.3411 | 3846.4455 | 3816.1705 | 3785.4206 | 3755.8633 | 3689.473
Pumped Storage Hydro | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD
Reciprocating Peaker | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD
Small Modular Nuclear | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD
Electrolyzer | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD | TBD

## Offshore Wind
Source material |  |  |  | Adjustments
| Base | Percentage of total CAPEX | Scale to 2021 NREL 2019 vintage, 2019 $ | PSE Adjustment 1: escalate to 2020 $ | PSE Adjustment 1 Total | PSE Adjustment 2: add Spur Line | PSE Adjustment 2 Total | PSE ADJUSTED CAPITAL COST | Notes
NREL ATB Nameplate (MW) | 1005
Capital Cost Component | $/kW | % of Total | $/kW | Multiplier | $/kW | Adder | $/kW | $/kW
Turbine capital costs
SUB TOTAL | 1301 | 24.42% | 1265.483 | 2.5% | 1297.1201 | 0 | 1297.1201 | 1297.1201
Balance of System
Development | 165 | 3.097% | 160.4955 | 2.5% | 164.5079 | 0 | 164.5079 | 164.5079
Engineering & Mgmt | 85 | 1.595% | 82.6795 | 2.5% | 84.7465 | 0 | 84.7465 | 84.7465
Substructure & foundation | 1438 | 26.99% | 1398.743 | 2.5% | 1433.7115 | 0 | 1433.7115 | 1433.7115
Port & staging,logistics,transport | 44 | 0.8258% | 42.7988 | 2.5% | 43.8688 | 0 | 43.8688 | 43.8688
electrical infrastructure | 979 | 18.37% | 952.2736 | 2.5% | 976.0804 | 2.4876 | 978.568 | 978.568 | added 5mi spur line for interconnection assumed at $500,000 per mile
Assembly & installation | 439 | 8.239% | 427.0154 | 2.5% | 437.6908 | 0 | 437.6908 | 437.6908
Lease price | 88 | 1.652% | 85.5976 | 2.5% | 87.7376 | 0 | 87.7376 | 87.7376
SUB TOTAL | 3237 | 60.75% | 3148.6307 | 2.5% | 3228.3435 | 0 | 3230.8311 | 3230.8311
Soft Costs
Insurance during construction | 52 | 0.976% | 50.5804 | 2.5% | 51.8449 | 0 | 51.8449 | 51.8449
Decommissioning bond | 76 | 1.426% | 73.9252 | 2.5% | 75.7734 | 0 | 75.7734 | 75.7734
construction financing | 221 | 4.148% | 214.9668 | 2.5% | 220.3409 | 0 | 220.3409 | 220.3409
contingency | 389 | 7.301% | 378.3804 | 2.5% | 387.8399 | 0 | 387.8399 | 387.8399
Plant commissioning | 52 | 0.976% | 50.5804 | 2.5% | 51.8449 | 0 | 51.8449 | 51.8449
SUB TOTAL | 790 | 14.83% | 768.4332 | 2.5% | 787.644 | 0 | 787.644 | 787.644
Total CAPEX | 5328 | 100% | 5182.547 | 2.5% | 5313.1077 | 0 | 5315.5952 | 5315.5952
↓ COST CURVE ↓
Year | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
2021 NREL ATB, Moderate Class 8 | 5182.547 | 4847.6935 | 4597.879 | 4394.6613 | 4220.917 | 4067.512 | 3928.9941 | 3801.8464 | 3683.6678 | 3572.7455 | 3467.815 | 3367.9158 | 3314.41 | 3264.5972 | 3218.0005 | 3174.2297 | 3132.9614 | 3093.925 | 3056.8913 | 3021.6649 | 2988.0776 | 2955.9835 | 2925.2555 | 2895.7821 | 2867.4649 | 2840.2164 | 2813.9591 | 2788.6232 | 2764.1463 | 2740.4721 | 2717.5496 | 2695.3326
% change on year | -- | 0.064612 | 0.051533 | 0.044198 | 0.039535 | 0.036344 | 0.034055 | 0.032361 | 0.031085 | 0.030112 | 0.02937 | 0.028808 | 0.015887 | 0.015029 | 0.014273 | 0.013602 | 0.013001 | 0.01246 | 0.01197 | 0.011524 | 0.011116 | 0.010741 | 0.010395 | 0.010075 | 0.0097788 | 0.0095026 | 0.0092448 | 0.0090036 | 0.0087774 | 0.0085647 | 0.0083644 | 0.0081754
After PSE Adjustments | 5315.5952 | 4972.1452 | 4715.9175 | 4507.4827 | 4329.2779 | 4171.9346 | 4029.8606 | 3899.4488 | 3778.2363 | 3664.4664 | 3556.842 | 3454.3781 | 3399.4987 | 3348.4072 | 3300.6142 | 3255.7197 | 3213.392 | 3173.3534 | 3135.369 | 3099.2382 | 3064.7886 | 3031.8706 | 3000.3538 | 2970.1237 | 2941.0795 | 2913.1315 | 2886.2 | 2860.2137 | 2835.1085 | 2810.8266 | 2787.3156 | 2764.5281

## Onshore Wind
Source material |  |  |  | Adjustments
| Base | Percentage of total CAPEX | Scale to 2021 NREL 2019 vintage, 2019 $ | PSE Adjustment 1: escalate to 2020 $ | PSE Adjustment 1 Total | PSE Adjustment 2: add Spur Line | PSE Adjustment 2 Total | PSE ADJUSTED CAPITAL COST | Notes
NREL ATB Nameplate (MW) | 200
Capital Cost Component | $/kW | % of Total | $/kW | Multiplier | $/kW | Adder | $/kW | $/kW
Turbine capital cost
Rotor module | 287 | 19.99% | 287 | 2.5% | 294.175 | 0 | 294.175 | 294.175
Nacelle module | 488 | 33.98% | 488 | 2.5% | 500.2 | 0 | 500.2 | 500.2
Tower module | 215 | 14.97% | 215 | 2.5% | 220.375 | 0 | 220.375 | 220.375
total | 991 | 69.01% | 991 | 2.5% | 1014.75 | 0 | 1014.75 | 1014.75
Balance of System
Dev cost | 16 | 1.114% | 16 | 2.5% | 16.4 | 0 | 16.4 | 16.4
Engineering & Mgmt | 18 | 1.253% | 18 | 2.5% | 18.45 | 0 | 18.45 | 18.45
Foundation | 59 | 4.109% | 59 | 2.5% | 60.475 | 0 | 60.475 | 60.475
Site access & staging | 44 | 3.064% | 44 | 2.5% | 45.1 | 0 | 45.1 | 45.1
Assembly & installation | 44 | 3.064% | 44 | 2.5% | 45.1 | 0 | 45.1 | 45.1
electrical infrastructure | 145 | 10.1% | 145 | 2.5% | 148.625 | 12.5 | 161.125 | 161.125 | added 5mi spur line for interconnection assumed at $500,000 per mile
Total | 326 | 22.7% | 326 | 2.5% | 334.15 | 0 | 346.65 | 346.65
financial costs
Construction financing | 34 | 2.368% | 34 | 2.5% | 34.85 | 0 | 34.85 | 34.85
Contingency fund | 86 | 5.989% | 86 | 2.5% | 88.15 | 0 | 88.15 | 88.15
Total | 120 | 8.357% | 120 | 2.5% | 123 | 0 | 123 | 123
Total CAPEX | 1436 | 100% | 1436 | 2.5% | 1471.9 | 0 | 1484.4 | 1484.4
↓ COST CURVE ↓
Year | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
2021 NREL ATB, Class 4 | 1436 | 1391.8182 | 1347.6364 | 1303.4545 | 1259.2727 | 1215.0909 | 1170.9091 | 1126.7273 | 1082.5455 | 1038.3636 | 994.1818 | 950 | 940.5 | 931 | 921.5 | 912 | 902.5 | 893 | 883.5 | 874 | 864.5 | 855 | 845.5 | 836 | 826.5 | 817 | 807.5 | 798 | 788.5 | 779 | 769.5 | 760
% change on year | -- | 0.030767 | 0.031744 | 0.032785 | 0.033896 | 0.035085 | 0.036361 | 0.037733 | 0.039213 | 0.040813 | 0.042549 | 0.04444 | 0.01 | 0.010101 | 0.010204 | 0.010309 | 0.010417 | 0.010526 | 0.010638 | 0.010753 | 0.01087 | 0.010989 | 0.011111 | 0.011236 | 0.011364 | 0.011494 | 0.011628 | 0.011765 | 0.011905 | 0.012048 | 0.012195 | 0.012346
After PSE Adjustments | 1484.4 | 1438.729 | 1393.0581 | 1347.3871 | 1301.7162 | 1256.0452 | 1210.3743 | 1164.7033 | 1119.0324 | 1073.3614 | 1027.6905 | 982.0195 | 972.1993 | 962.3791 | 952.5589 | 942.7387 | 932.9185 | 923.0983 | 913.2781 | 903.4579 | 893.6377 | 883.8175 | 873.9974 | 864.1772 | 854.357 | 844.5368 | 834.7166 | 824.8964 | 815.0762 | 805.256 | 795.4358 | 785.6156

## Solar_Utility
Source material |  |  |  | Adjustments
| Base | Percentage of total CAPEX | Scale to 2021 NREL 2019 vintage, 2019 $ | PSE Adjustment 1: escalate to 2020 $ | PSE Adjustment 1 Total | PSE Adjustment 2: add Spur Line | PSE Adjustment 2 Total | PSE ADJUSTED CAPITAL COST
NREL ATB Nameplate (MW) | 134 | % of Total | $/kW | Multiplier | $/kW | adder | $/kW | $/kW
Module component | Cost in $, rough
Module | 41000000 | 40.59% | 564.728 | 2.5% | 578.8462 | 0 | 578.8462 | 578.8462
Inverter | 5000000 | 4.95% | 68.8693 | 2.5% | 70.591 | 0 | 70.591 | 70.591
Structural BOS | 12000000 | 11.88% | 165.2862 | 2.5% | 169.4184 | 0 | 169.4184 | 169.4184
Electrical BOS | 7000000 | 6.931% | 96.417 | 2.5% | 98.8274 | 0 | 98.8274 | 98.8274
Total BOS | 19000000 | 18.81% | 261.7032 | 2.5% | 268.2458 | 0 | 268.2458 | 268.2458
Install labor & equipment | 11000000 | 10.89% | 151.5124 | 2.5% | 155.3002 | 0 | 155.3002 | 155.3002
EPC overhead | 6000000 | 5.941% | 82.6431 | 2.5% | 84.7092 | 0 | 84.7092 | 84.7092
Sales tax | 4000000 | 3.96% | 55.0954 | 2.5% | 56.4728 | 0 | 56.4728 | 56.4728
Total EPC | 86000000 | 85.15% | 1184.5514 | 2.5% | 1214.1652 | 0 | 1214.1652 | 1214.1652
Land
Permitting fee
Interconnection fee | 3000000 | 2.97% | 41.3216 | 2.5% | 42.3546 | 0 | 42.3546 | 42.3546
Transmission line | 2000000 | 1.98% | 27.5477 | 2.5% | 28.2364 | 3.7313 | 31.9677 | 31.9677 | adjusted for 5mi spur line for interconnection assumed at $500,000 per mile; base assumption assumes ~4mi spur ($2,000,000)
Developer overhead | 2000000 | 1.98% | 27.5477 | 2.5% | 28.2364 | 0 | 28.2364 | 28.2364
Contingency | 3000000 | 2.97% | 41.3216 | 2.5% | 42.3546 | 0 | 42.3546 | 42.3546
EPC/developer profit | 5000000 | 4.95% | 68.8693 | 2.5% | 70.591 | 0 | 70.591 | 70.591
Developer cost | 15000000 | 14.85% | 206.6078 | 2.5% | 211.773 | 0 | 215.5043 | 215.5043
Total | 101000000 | 100% | 1391.1592 | 2.5% | 1425.9382 | 0 | 1429.6696 | 1429.6696
↓ COST CURVE ↓
Year | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
NREL ATB Listing | 1391.1592 | 1376.5401 | 1316.4772 | 1256.4142 | 1196.3513 | 1136.2883 | 1076.2254 | 1016.1624 | 956.0995 | 896.0365 | 835.9736 | 775.9106 | 768.9966 | 762.0826 | 755.1685 | 748.2545 | 741.3405 | 734.4264 | 727.5124 | 720.5984 | 713.6844 | 706.7703 | 699.8563 | 692.9423 | 686.0283 | 679.1142 | 672.2002 | 665.2862 | 658.3721 | 651.4581 | 644.5441 | 637.6301
% change on year | -- | 0.010509 | 0.043633 | 0.045624 | 0.047805 | 0.050205 | 0.052859 | 0.055809 | 0.059108 | 0.062821 | 0.067032 | 0.071848 | 0.0089109 | 0.008991 | 0.0090725 | 0.0091556 | 0.0092402 | 0.0093264 | 0.0094142 | 0.0095037 | 0.0095948 | 0.0096878 | 0.0097826 | 0.0098792 | 0.0099778 | 0.010078 | 0.010181 | 0.010286 | 0.010393 | 0.010502 | 0.010613 | 0.010727
After PSE Adjustments | 1429.6696 | 1414.6458 | 1352.9201 | 1291.1945 | 1229.4689 | 1167.7433 | 1106.0176 | 1044.292 | 982.5664 | 920.8408 | 859.1151 | 797.3895 | 790.2841 | 783.1787 | 776.0732 | 768.9678 | 761.8624 | 754.757 | 747.6515 | 740.5461 | 733.4407 | 726.3353 | 719.2299 | 712.1244 | 705.019 | 697.9136 | 690.8082 | 683.7027 | 676.5973 | 669.4919 | 662.3865 | 655.281

## Solar_Residential
Source material |  |  |  | Adjustments
| Base | Percentage of total CAPEX | Scale to 2021 NREL 2019 vintage, 2019 $ | PSE Adjustment 1: escalate to 2020 $ | PSE Adjustment 1 Total | PSE ADJUSTED CAPITAL COST
NREL ATB Nameplate (MW) | 134 | % of Total | $/kW | Multiplier | $/kW | $/kW
Module component | Cost in $, rough
PV modules | 2844 | 16.66% | 462.0615 | 2.5% | 473.613 | 473.613
Lithium-ion battery | 0 | 0% | 0 | 2.5% | 0 | 0
PV inverter | 1754 | 10.28% | 284.9704 | 2.5% | 292.0947 | 292.0947
Battery inverter | 0 | 0% | 0 | 2.5% | 0 | 0
Structural BOS | 589 | 3.45% | 95.6942 | 2.5% | 98.0865 | 98.0865
Electrical BOS | 1600 | 9.373% | 259.9502 | 2.5% | 266.4489 | 266.4489
Supply chain costs | 1825 | 10.69% | 296.5057 | 2.5% | 303.9183 | 303.9183
Sales tax | 440 | 2.578% | 71.4863 | 2.5% | 73.2735 | 73.2735
Installed Labor & equipment | 1309 | 7.668% | 212.6718 | 2.5% | 217.9885 | 217.9885
Permitting, inspection, interconnection | 1668 | 9.772% | 270.9981 | 2.5% | 277.773 | 277.773
Sales & Marketing | 2996 | 17.55% | 486.7567 | 2.5% | 498.9257 | 498.9257
Net profit | 2045 | 11.98% | 332.2488 | 2.5% | 340.5551 | 340.5551
Total | 17070 | 100% | 2773.3436 | 2.5% | 2842.6772 | 2842.6772
↓ COST CURVE ↓
Year | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
NREL ATB Listing | 2773.3436 | 2710.1387 | 2539.5327 | 2368.9266 | 2198.3206 | 2027.7146 | 1857.1086 | 1686.5025 | 1515.8965 | 1345.2905 | 1174.6845 | 1004.0785 | 992.9479 | 981.8173 | 970.6868 | 959.5562 | 948.4257 | 937.2951 | 926.1645 | 915.034 | 903.9034 | 892.7729 | 881.6423 | 870.5117 | 859.3812 | 848.2506 | 837.1201 | 825.9895 | 814.859 | 803.7284 | 792.5978 | 781.4673
% change on year | -- | 0.02279 | 0.062951 | 0.06718 | 0.072018 | 0.077607 | 0.084137 | 0.091866 | 0.10116 | 0.11254 | 0.12682 | 0.14524 | 0.011085 | 0.01121 | 0.011337 | 0.011467 | 0.0116 | 0.011736 | 0.011875 | 0.012018 | 0.012164 | 0.012314 | 0.012467 | 0.012625 | 0.012786 | 0.012952 | 0.013122 | 0.013296 | 0.013475 | 0.013659 | 0.013849 | 0.014043
After PSE Adjustments | 2842.6772 | 2777.8922 | 2603.021 | 2428.1498 | 2253.2786 | 2078.4075 | 1903.5363 | 1728.6651 | 1553.7939 | 1378.9228 | 1204.0516 | 1029.1804 | 1017.7716 | 1006.3628 | 994.9539 | 983.5451 | 972.1363 | 960.7275 | 949.3187 | 937.9098 | 926.501 | 915.0922 | 903.6834 | 892.2745 | 880.8657 | 869.4569 | 858.0481 | 846.6392 | 835.2304 | 823.8216 | 812.4128 | 801.004

## Battery_Utility
Source material |  |  |  | Adjustments | [7 empty] | Source material |  |  |  |  | Adjustments | [7 empty] | Source material |  |  |  |  | Adjustments
| Base | Percentage of total CAPEX | Scale to 2021 NREL 2019 vintage, 2019 $ | PSE Adjustment 1: escalate to 2020 $ | PSE Adjustment 1 Total | PSE Adjustment 2: Overbuild Storage Block | PSE Adjustment 2 Total | PSE Adjustment 3: add Spur line | PSE Adjustment 3 Total | PSE ADJUSTED CAPITAL COST | Notes |  |  | Base | Percentage of total CAPEX | Scale to 2021 NREL 2019 vintage, 2019 $ | PSE Adjustment 1: escalate to 2020 $ | PSE Adjustment 1 Total | PSE Adjustment 2: Overbuild Storage Block | PSE Adjustment 2 Total | PSE Adjustment 3: add Spur line | PSE Adjustment 3 Total | PSE ADJUSTED CAPITAL COST | Notes |  |  | Base | Percentage of total CAPEX | Scale to 2021 NREL 2019 vintage, 2019 $ | PSE Adjustment 1: escalate to 2020 $ | PSE Adjustment 1 Total | PSE Adjustment 2: Overbuild Storage Block | PSE Adjustment 2 Total | PSE Adjustment 3: add Spur line | PSE Adjustment 3 Total | PSE ADJUSTED CAPITAL COST | Notes
NREL ATB Nameplate (MW) | 60 | [10 empty] | NREL ATB Nameplate (MW) |  | 60 | [10 empty] | NREL ATB Nameplate (MW) |  | 60
Duration (Hours) | 2 | [10 empty] | Duration (Hours) |  | 4 | [10 empty] | Duration (Hours) |  | 6
Lithium Ion Batteries | [11 empty] | Lithium Ion Batteries | [12 empty] | Lithium Ion Batteries
Duration | [11 empty] | Duration | [12 empty] | Duration
Module Component | $/kW | % of Total | $/kW | Multiplier | $/kW | Multiplier | $/kW | Adder | $/kW | $/kW |  | Module Component |  | $/kW | % of Total | $/kW | Multiplier | $/kW | Multiplier | $/kW | Adder | $/kW | $/kW |  | Module Component |  | $/kW | % of Total | $/kW | Multiplier | $/kW | Multiplier | $/kW | Adder | $/kW | $/kW
Storage Block | 336 | 39.34% | 335.7872 | 2.5% | 344.1819 | 20% | 413.0183 | 0 | 413.0183 | 413.0183 | overbuild storage capacity to allow for full battery duraction, assumes 20% increase in cells to account for 20% recommended minimum state of charge | Storage Block |  | 660 | 42.83% | 614.2949 | 2.5% | 629.6523 | 20% | 755.5828 | 0 | 755.5828 | 755.5828 | overbuild storage capacity to allow for full battery duraction, assumes 20% increase in cells to account for 20% recommended minimum state of charge | Storage Block |  | 984 | 44.32% | 893.1848 | 2.5% | 915.5144 | 20% | 1098.6173 | 0 | 1098.6173 | 1098.6173 | overbuild storage capacity to allow for full battery duraction, assumes 20% increase in cells to account for 20% recommended minimum state of charge
Storage balance of system | 82 | 9.602% | 81.9481 | 2.5% | 83.9968 | -- | 83.9968 | 0 | 83.9968 | 83.9968 |  | Storage balance of system |  | 152 | 9.864% | 141.474 | 2.5% | 145.0108 | -- | 145.0108 | 0 | 145.0108 | 145.0108 |  | Storage balance of system |  | 222 | 10% | 201.5112 | 2.5% | 206.549 | -- | 206.549 | 0 | 206.549 | 206.549
Power Equipment | 63 | 7.377% | 62.9601 | 2.5% | 64.5341 | -- | 64.5341 | 0 | 64.5341 | 64.5341 |  | Power Equipment |  | 63 | 4.088% | 58.6372 | 2.5% | 60.1032 | -- | 60.1032 | 0 | 60.1032 | 60.1032 |  | Power Equipment |  | 63 | 2.838% | 57.1856 | 2.5% | 58.6153 | -- | 58.6153 | 0 | 58.6153 | 58.6153
Controls & communication | 2 | 0.2342% | 1.9987 | 2.5% | 2.0487 | -- | 2.0487 | 0 | 2.0487 | 2.0487 |  | Controls & communication |  | 2 | 0.1298% | 1.8615 | 2.5% | 1.908 | -- | 1.908 | 0 | 1.908 | 1.908 |  | Controls & communication |  | 2 | 0.09009% | 1.8154 | 2.5% | 1.8608 | -- | 1.8608 | 0 | 1.8608 | 1.8608
System integration | 96 | 11.24% | 95.9392 | 2.5% | 98.3377 | -- | 98.3377 | 0 | 98.3377 | 98.3377 |  | System integration |  | 176 | 11.42% | 163.812 | 2.5% | 167.9073 | -- | 167.9073 | 0 | 167.9073 | 167.9073 |  | System integration |  | 252 | 11.35% | 228.7424 | 2.5% | 234.461 | -- | 234.461 | 0 | 234.461 | 234.461
Eng., procurement, construction | 116 | 13.58% | 115.9265 | 2.5% | 118.8247 | -- | 118.8247 | 0 | 118.8247 | 118.8247 |  | Eng., procurement, construction |  | 212 | 13.76% | 197.319 | 2.5% | 202.252 | -- | 202.252 | 0 | 202.252 | 202.252 |  | Eng., procurement, construction |  | 306 | 13.78% | 277.7587 | 2.5% | 284.7026 | -- | 284.7026 | 0 | 284.7026 | 284.7026
Project Dev | 140 | 16.39% | 139.9113 | 2.5% | 143.4091 | -- | 143.4091 | 0 | 143.4091 | 143.4091 |  | Project Dev |  | 252 | 16.35% | 234.549 | 2.5% | 240.4127 | -- | 240.4127 | 0 | 240.4127 | 240.4127 |  | Project Dev |  | 366 | 16.49% | 332.2212 | 2.5% | 340.5267 | -- | 340.5267 | 0 | 340.5267 | 340.5267
Grid integration | 20 | 2.342% | 19.9873 | 2.5% | 20.487 | -- | 20.487 | 41.6667 | 62.1537 | 62.1537 | added 5mi spur line for interconnection assumed at $500,000 per mile | Grid integration |  | 20 | 1.298% | 18.615 | 2.5% | 19.0804 | -- | 19.0804 | 41.6667 | 60.747 | 60.747 | added 5mi spur line for interconnection assumed at $500,000 per mile | Grid integration |  | 20 | 0.9009% | 18.1542 | 2.5% | 18.608 | -- | 18.608 | 41.6667 | 60.2747 | 60.2747 | added 5mi spur line for interconnection assumed at $500,000 per mile
Total ESS intalled cost | 854 | 100% | 853.4592 | 2.5% | 875.82 | -- | 944.6564 | 0 | 986.3231 | 986.3231 |  | Total ESS intalled cost |  | 1541 | 100% | 1434.2856 | 2.5% | 1466.3267 | -- | 1592.2571 | 0 | 1633.9238 | 1633.9238 |  | Total ESS intalled cost |  | 2220 | 100% | 2015.112 | 2.5% | 2065.4898 | -- | 2243.9407 | 0 | 2285.6073 | 2285.6073
↓ COST CURVES ↓
2hr LI
Year | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
NREL ATB Listing | 853.4592 | 810.0348 | 763.3964 | 716.7579 | 670.1194 | 623.4809 | 576.8425 | 559.5765 | 542.3105 | 525.0444 | 507.7784 | 490.5124 | 485.2256 | 479.9387 | 474.6518 | 469.3649 | 464.078 | 458.7911 | 453.5043 | 448.2174 | 442.9305 | 437.6436 | 432.3567 | 427.0698 | 421.783 | 416.4961 | 411.2092 | 405.9223 | 400.6354 | 395.3485 | 390.0617 | 384.7748
% change on year | -- | 0.05088 | 0.057576 | 0.061093 | 0.065069 | 0.069597 | 0.074803 | 0.029932 | 0.030855 | 0.031838 | 0.032885 | 0.034003 | 0.010778 | 0.010896 | 0.011016 | 0.011138 | 0.011264 | 0.011392 | 0.011524 | 0.011658 | 0.011795 | 0.011936 | 0.01208 | 0.012228 | 0.012379 | 0.012535 | 0.012694 | 0.012857 | 0.013024 | 0.013196 | 0.013373 | 0.013554
After PSE Adjustments | 986.3231 | 936.1386 | 882.2395 | 828.3405 | 774.4415 | 720.5425 | 666.6435 | 646.6896 | 626.7357 | 606.7817 | 586.8278 | 566.8739 | 560.764 | 554.654 | 548.5441 | 542.4342 | 536.3243 | 530.2143 | 524.1044 | 517.9945 | 511.8845 | 505.7746 | 499.6647 | 493.5547 | 487.4448 | 481.3349 | 475.225 | 469.115 | 463.0051 | 456.8952 | 450.7852 | 444.6753
4hr LI
Year | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
NREL ATB Listing | 1434.2856 | 1363.2842 | 1281.8131 | 1200.3419 | 1118.8707 | 1037.3996 | 955.9284 | 921.5615 | 887.1946 | 852.8276 | 818.4607 | 784.0938 | 774.2926 | 764.4915 | 754.6903 | 744.8891 | 735.088 | 725.2868 | 715.4856 | 705.6844 | 695.8833 | 686.0821 | 676.2809 | 666.4797 | 656.6786 | 646.8774 | 637.0762 | 627.2751 | 617.4739 | 607.6727 | 597.8715 | 588.0704
% change on year | -- | 0.049503 | 0.059761 | 0.063559 | 0.067873 | 0.072816 | 0.078534 | 0.035951 | 0.037292 | 0.038737 | 0.040298 | 0.04199 | 0.0125 | 0.012658 | 0.012821 | 0.012987 | 0.013158 | 0.013333 | 0.013514 | 0.013699 | 0.013889 | 0.014085 | 0.014286 | 0.014493 | 0.014706 | 0.014925 | 0.015152 | 0.015385 | 0.015625 | 0.015873 | 0.016129 | 0.016393
After PSE Adjustments | 1633.9238 | 1553.0397 | 1460.2286 | 1367.4175 | 1274.6063 | 1181.7952 | 1088.984 | 1049.8336 | 1010.6832 | 971.5327 | 932.3823 | 893.2318 | 882.0664 | 870.901 | 859.7356 | 848.5702 | 837.4048 | 826.2394 | 815.074 | 803.9086 | 792.7432 | 781.5779 | 770.4125 | 759.2471 | 748.0817 | 736.9163 | 725.7509 | 714.5855 | 703.4201 | 692.2547 | 681.0893 | 669.9239
6hr LI
Year | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
NREL ATB Listing | 2015.112 | 1916.5336 | 1800.2298 | 1683.9259 | 1567.622 | 1451.3182 | 1335.0143 | 1283.5465 | 1232.0787 | 1180.6108 | 1129.143 | 1077.6752 | 1063.3597 | 1049.0443 | 1034.7288 | 1020.4134 | 1006.0979 | 991.7824 | 977.467 | 963.1515 | 948.836 | 934.5206 | 920.2051 | 905.8897 | 891.5742 | 877.2587 | 862.9433 | 848.6278 | 834.3123 | 819.9969 | 805.6814 | 791.366
% change on year | -- | 0.04892 | 0.060684 | 0.064605 | 0.069067 | 0.074191 | 0.080137 | 0.038552 | 0.040098 | 0.041773 | 0.043594 | 0.045581 | 0.013284 | 0.013462 | 0.013646 | 0.013835 | 0.014029 | 0.014229 | 0.014434 | 0.014645 | 0.014863 | 0.015087 | 0.015319 | 0.015557 | 0.015803 | 0.016056 | 0.016318 | 0.016589 | 0.016869 | 0.017158 | 0.017458 | 0.017768
After PSE Adjustments | 2285.6073 | 2173.7965 | 2041.8807 | 1909.965 | 1778.0493 | 1646.1336 | 1514.2178 | 1455.8413 | 1397.4648 | 1339.0883 | 1280.7117 | 1222.3352 | 1206.0981 | 1189.8611 | 1173.624 | 1157.3869 | 1141.1498 | 1124.9128 | 1108.6757 | 1092.4386 | 1076.2015 | 1059.9645 | 1043.7274 | 1027.4903 | 1011.2532 | 995.0162 | 978.7791 | 962.542 | 946.3049 | 930.0679 | 913.8308 | 897.5937

## Battery_Residential
Source material |  |  |  | Adjustments
| Base | Percentage of total CAPEX | Scale to 2021 NREL 2019 vintage, 2019 $ | PSE Adjustment 1: escalate to 2020 $ | PSE Adjustment 1 Total | PSE ADJUSTED CAPITAL COST
NREL ATB Nameplate (MW) | 5 kW, 14.5 kWh | % of Total | $/kW | Multiplier | $/kW | $/kW
Module component | $
Lithium Ion Battery | 3479 | 18.56% | 829.2557 | 2.5% | 849.987 | 849.987
Battery Inverter | 2393 | 12.77% | 570.3963 | 2.5% | 584.6562 | 584.6562
Electrical BOS | 1507 | 8.041% | 359.209 | 2.5% | 368.1893 | 368.1893
Suuply Chain Costs | 369 | 1.969% | 87.955 | 2.5% | 90.1538 | 90.1538
Sales Tax | 535 | 2.855% | 127.5228 | 2.5% | 130.7109 | 130.7109
Install Labor and Equipment | 1560 | 8.324% | 371.8421 | 2.5% | 381.1382 | 381.1382
Permitting, Inspection, Interconnection | 1209 | 6.451% | 288.1777 | 2.5% | 295.3821 | 295.3821
Overhead | 1940 | 10.35% | 462.4191 | 2.5% | 473.9796 | 473.9796
Sales and Marketing | 3829 | 20.43% | 912.6818 | 2.5% | 935.4988 | 935.4988
Net Profit | 1920 | 10.24% | 457.6519 | 2.5% | 469.0932 | 469.0932
TOTAL | 18741 | 100% | 4467.1113 | 2.5% | 4578.7891 | 4578.7891
↓ COST CURVE ↓
Year | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
NREL ATB Listing | 4467.1113 | 4213.2444 | 3983.0155 | 3752.3994 | 3543.05 | 3350.4969 | 3171.1765 | 3070.3819 | 2980.2894 | 2901.6634 | 2825.0794 | 2755.5049 | 2721.0611 | 2686.6172 | 2652.1734 | 2617.7296 | 2583.2858 | 2548.842 | 2514.3982 | 2479.9544 | 2445.5106 | 2411.0668 | 2376.6229 | 2342.1791 | 2307.7353 | 2273.2915 | 2238.8477 | 2204.4039 | 2169.9601 | 2135.5163 | 2101.0725 | 2066.6287
% change on year | -- | 0.05683 | 0.054644 | 0.0579 | 0.055791 | 0.054347 | 0.053521 | 0.031785 | 0.029342 | 0.026382 | 0.026393 | 0.024627 | 0.0125 | 0.012658 | 0.012821 | 0.012987 | 0.013158 | 0.013333 | 0.013514 | 0.013699 | 0.013889 | 0.014085 | 0.014286 | 0.014493 | 0.014706 | 0.014925 | 0.015152 | 0.015385 | 0.015625 | 0.015873 | 0.016129 | 0.016393
After PSE Adjustments | 4578.7891 | 4318.5755 | 4082.5909 | 3846.2094 | 3631.6263 | 3434.2594 | 3250.4559 | 3147.1414 | 3054.7966 | 2974.205 | 2895.7063 | 2824.3925 | 2789.0876 | 2753.7827 | 2718.4778 | 2683.1729 | 2647.868 | 2612.5631 | 2577.2581 | 2541.9532 | 2506.6483 | 2471.3434 | 2436.0385 | 2400.7336 | 2365.4287 | 2330.1238 | 2294.8189 | 2259.514 | 2224.2091 | 2188.9042 | 2153.5993 | 2118.2944

## Hybrid
| Solar + Battery |  | Benefit | 8.862% |  |  | Wind + Battery |  | Benefit | 7.893% |  |  | Wind + Solar + Battery |  | Benefit | 8.868%
| Battery Components | PSE Adjusted Cost, $/kW | Savings, % | Hybrid Cost, $/kW |  |  | Battery Components | PSE Adjusted Cost, $/kW | Savings, % | Hybrid Cost, $/kW |  |  | Battery Components | PSE Adjusted Cost, $/kW | Savings, % | Hybrid Cost, $/kW
| Storage Block | 755.5828 | 0 | 755.5828 |  |  | Storage Block | 755.5828 | 0 | 755.5828 |  |  | Storage Block | 755.5828 | 0 | 755.5828
| Storage balance of system | 145.0108 | 0 | 145.0108 |  |  | Storage balance of system | 145.0108 | 0 | 145.0108 |  |  | Storage balance of system | 145.0108 | 0 | 145.0108
| Power Equipment | 60.1032 | 0 | 60.1032 |  |  | Power Equipment | 60.1032 | 0 | 60.1032 |  |  | Power Equipment | 60.1032 | 0 | 60.1032
| Controls & communication | 1.908 | 0 | 1.908 |  |  | Controls & communication | 1.908 | 0 | 1.908 |  |  | Controls & communication | 1.908 | 0 | 1.908
| System integration | 167.9073 | 0.5 | 83.9536 |  |  | System integration | 167.9073 | 0.5 | 83.9536 |  |  | System integration | 167.9073 | 0.5 | 83.9536
| Eng., procurement, construction | 202.252 | 0 | 202.252 |  |  | Eng., procurement, construction | 202.252 | 0 | 202.252 |  |  | Eng., procurement, construction | 202.252 | 0 | 202.252
| Project Dev | 240.4127 | 0 | 240.4127 |  |  | Project Dev | 240.4127 | 0 | 240.4127 |  |  | Project Dev | 240.4127 | 0 | 240.4127
| Grid integration | 60.747 | 0.5 | 30.3735 |  |  | Grid integration | 60.747 | 0.5 | 30.3735 |  |  | Grid integration | 60.747 | 0.5 | 30.3735
| Total | 1633.9238 |  | 1519.5966 |  |  | Total | 1633.9238 |  | 1519.5966 |  |  | Total | 1633.9238 |  | 1519.5966
| Solar Components | PSE Adjusted Cost, $/kW | Savings, % | Hybrid Cost, $/kW |  |  | Wind Components | PSE Adjusted Cost, $/kW | Savings, % | Hybrid Cost, $/kW |  |  | Solar Components | PSE Adjusted Cost, $/kW | Savings, % | Hybrid Cost, $/kW
| Module | 578.8462 | 0 | 578.8462 |  |  | Rotor module | 294.175 | 0 | 294.175 |  |  | Module | 578.8462 | 0 | 578.8462
| Inverter | 70.591 | 0 | 70.591 |  |  | Nacelle module | 500.2 | 0 | 500.2 |  |  | Inverter | 70.591 | 0 | 70.591
| Structural BOS | 169.4184 | 0 | 169.4184 |  |  | Tower module | 220.375 | 0 | 220.375 |  |  | Structural BOS | 169.4184 | 0 | 169.4184
| Electrical BOS | 98.8274 | 0 | 98.8274 |  |  | Dev cost | 16.4 | 0.5 | 8.2 |  |  | Electrical BOS | 98.8274 | 0 | 98.8274
| Install labor & equipment | 155.3002 | 0.5 | 77.6501 |  |  | Engineering & Mgmt | 18.45 | 0.5 | 9.225 |  |  | Install labor & equipment | 155.3002 | 0.5 | 77.6501
| EPC overhead | 84.7092 | 0.5 | 42.3546 |  |  | Foundation | 60.475 | 0 | 60.475 |  |  | EPC overhead | 84.7092 | 0.5 | 42.3546
| Sales tax | 56.4728 | 0 | 56.4728 |  |  | Site access & staging | 45.1 | 0.5 | 22.55 |  |  | Sales tax | 56.4728 | 0 | 56.4728
| Land | 0 | 0 | 0 |  |  | Assembly & installation | 45.1 | 0.25 | 33.825 |  |  | Land | 0 | 0 | 0
| Permitting fee | 0 | 0 | 0 |  |  | electrical infrastructure | 161.125 | 0.5 | 80.5625 |  |  | Permitting fee | 0 | 0 | 0
| Interconnection fee | 42.3546 | 0.5 | 21.1773 |  |  | Construction financing | 34.85 | 0 | 34.85 |  |  | Interconnection fee | 42.3546 | 0.5 | 21.1773
| Transmission line | 31.9677 | 0.5 | 15.9839 |  |  | Contingency fund | 88.15 | 0 | 88.15 |  |  | Transmission line | 31.9677 | 0.5 | 15.9839
| Developer overhead | 28.2364 | 0 | 28.2364 |  |  | Total | 1484.4 |  | 1352.5875 |  |  | Developer overhead | 28.2364 | 0 | 28.2364
| Contingency | 42.3546 | 0 | 42.3546 | [8 empty] | Contingency | 42.3546 | 0 | 42.3546
| EPC/developer profit | 70.591 | 0 | 70.591 | [8 empty] | EPC/developer profit | 70.591 | 0 | 70.591
| Total | 1429.6696 |  | 1272.5037 | [8 empty] | Total | 1429.6696 |  | 1272.5037
[13 empty] | Wind Components | PSE Adjusted Cost, $/kW | Savings, % | Hybrid Cost, $/kW
[13 empty] | Rotor module | 294.175 | 0 | 294.175
[13 empty] | Nacelle module | 500.2 | 0 | 500.2
[13 empty] | Tower module | 220.375 | 0 | 220.375
[13 empty] | Dev cost | 16.4 | 0.5 | 8.2
[13 empty] | Engineering & Mgmt | 18.45 | 0.5 | 9.225
[13 empty] | Foundation | 60.475 | 0 | 60.475
[13 empty] | Site access & staging | 45.1 | 0.5 | 22.55
[13 empty] | Assembly & installation | 45.1 | 0.25 | 33.825
[13 empty] | electrical infrastructure | 161.125 | 0.5 | 80.5625
[13 empty] | Construction financing | 34.85 | 0 | 34.85
[13 empty] | Contingency fund | 88.15 | 0 | 88.15
[13 empty] | Total | 1484.4 |  | 1352.5875
↓ COST CURVE ↓
Year | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
Solar - NREL ATB | 1391.1592 | 1376.5401 | 1316.4772 | 1256.4142 | 1196.3513 | 1136.2883 | 1076.2254 | 1016.1624 | 956.0995 | 896.0365 | 835.9736 | 775.9106 | 768.9966 | 762.0826 | 755.1685 | 748.2545 | 741.3405 | 734.4264 | 727.5124 | 720.5984 | 713.6844 | 706.7703 | 699.8563 | 692.9423 | 686.0283 | 679.1142 | 672.2002 | 665.2862 | 658.3721 | 651.4581 | 644.5441 | 637.6301
Solar - % change on year | -- | 0.010509 | 0.043633 | 0.045624 | 0.047805 | 0.050205 | 0.052859 | 0.055809 | 0.059108 | 0.062821 | 0.067032 | 0.071848 | 0.0089109 | 0.008991 | 0.0090725 | 0.0091556 | 0.0092402 | 0.0093264 | 0.0094142 | 0.0095037 | 0.0095948 | 0.0096878 | 0.0097826 | 0.0098792 | 0.0099778 | 0.010078 | 0.010181 | 0.010286 | 0.010393 | 0.010502 | 0.010613 | 0.010727
Solar - PSE | 1272.5037 | 1259.1315 | 1204.1914 | 1149.2514 | 1094.3114 | 1039.3714 | 984.4313 | 929.4913 | 874.5513 | 819.6113 | 764.6712 | 709.7312 | 703.4069 | 697.0826 | 690.7583 | 684.434 | 678.1096 | 671.7853 | 665.461 | 659.1367 | 652.8124 | 646.4881 | 640.1638 | 633.8394 | 627.5151 | 621.1908 | 614.8665 | 608.5422 | 602.2179 | 595.8936 | 589.5693 | 583.2449
Battery - NREL ATB | 1434.2856 | 1363.2842 | 1281.8131 | 1200.3419 | 1118.8707 | 1037.3996 | 955.9284 | 921.5615 | 887.1946 | 852.8276 | 818.4607 | 784.0938 | 774.2926 | 764.4915 | 754.6903 | 744.8891 | 735.088 | 725.2868 | 715.4856 | 705.6844 | 695.8833 | 686.0821 | 676.2809 | 666.4797 | 656.6786 | 646.8774 | 637.0762 | 627.2751 | 617.4739 | 607.6727 | 597.8715 | 588.0704
Battery - % change on year | -- | 0.049503 | 0.059761 | 0.063559 | 0.067873 | 0.072816 | 0.078534 | 0.035951 | 0.037292 | 0.038737 | 0.040298 | 0.04199 | 0.0125 | 0.012658 | 0.012821 | 0.012987 | 0.013158 | 0.013333 | 0.013514 | 0.013699 | 0.013889 | 0.014085 | 0.014286 | 0.014493 | 0.014706 | 0.014925 | 0.015152 | 0.015385 | 0.015625 | 0.015873 | 0.016129 | 0.016393
Battery - PSE | 1519.5966 | 1444.3721 | 1358.0551 | 1271.738 | 1185.4209 | 1099.1039 | 1012.7868 | 976.3758 | 939.9647 | 903.5537 | 867.1426 | 830.7316 | 820.3474 | 809.9633 | 799.5791 | 789.195 | 778.8108 | 768.4267 | 758.0426 | 747.6584 | 737.2743 | 726.8901 | 716.506 | 706.1218 | 695.7377 | 685.3535 | 674.9694 | 664.5853 | 654.2011 | 643.817 | 633.4328 | 623.0487
Wind - NREL ATB | 1436 | 1391.8182 | 1347.6364 | 1303.4545 | 1259.2727 | 1215.0909 | 1170.9091 | 1126.7273 | 1082.5455 | 1038.3636 | 994.1818 | 950 | 940.5 | 931 | 921.5 | 912 | 902.5 | 893 | 883.5 | 874 | 864.5 | 855 | 845.5 | 836 | 826.5 | 817 | 807.5 | 798 | 788.5 | 779 | 769.5 | 760
Wind - % change on year | -- | 0.030767 | 0.031744 | 0.032785 | 0.033896 | 0.035085 | 0.036361 | 0.037733 | 0.039213 | 0.040813 | 0.042549 | 0.04444 | 0.01 | 0.010101 | 0.010204 | 0.010309 | 0.010417 | 0.010526 | 0.010638 | 0.010753 | 0.01087 | 0.010989 | 0.011111 | 0.011236 | 0.011364 | 0.011494 | 0.011628 | 0.011765 | 0.011905 | 0.012048 | 0.012195 | 0.012346
Wind - PSE | 1352.5875 | 1310.9721 | 1269.3566 | 1227.7412 | 1186.1257 | 1144.5103 | 1102.8948 | 1061.2794 | 1019.664 | 978.0485 | 936.4331 | 894.8176 | 885.8695 | 876.9213 | 867.9731 | 859.0249 | 850.0768 | 841.1286 | 832.1804 | 823.2322 | 814.284 | 805.3359 | 796.3877 | 787.4395 | 778.4913 | 769.5432 | 760.595 | 751.6468 | 742.6986 | 733.7505 | 724.8023 | 715.8541
100 MW Solar + 50 MW Battery | 1354.868 | 1320.8784 | 1255.4793 | 1190.0803 | 1124.6812 | 1059.2822 | 993.8832 | 945.1195 | 896.3558 | 847.5921 | 798.8284 | 750.0647 | 742.3871 | 734.7095 | 727.0319 | 719.3543 | 711.6767 | 703.9991 | 696.3215 | 688.6439 | 680.9663 | 673.2888 | 665.6112 | 657.9336 | 650.256 | 642.5784 | 634.9008 | 627.2232 | 619.5456 | 611.868 | 604.1904 | 596.5129
100 MW Wind + 50 MW Battery | 1408.2572 | 1355.4387 | 1298.9228 | 1242.4068 | 1185.8908 | 1129.3748 | 1072.8588 | 1032.9782 | 993.0975 | 953.2169 | 913.3363 | 873.4556 | 864.0288 | 854.6019 | 845.1751 | 835.7483 | 826.3215 | 816.8946 | 807.4678 | 798.041 | 788.6141 | 779.1873 | 769.7605 | 760.3336 | 750.9068 | 741.48 | 732.0531 | 722.6263 | 713.1995 | 703.7726 | 694.3458 | 684.919
100 MW Wind + 100 MW Solar + 50 MW Battery | 1692.4448 | 1646.1448 | 1576.2878 | 1506.4308 | 1436.5738 | 1366.7168 | 1296.8598 | 1239.4793 | 1182.0988 | 1124.7183 | 1067.3378 | 1009.9573 | 999.725 | 989.4928 | 979.2605 | 969.0282 | 958.7959 | 948.5636 | 938.3313 | 928.0991 | 917.8668 | 907.6345 | 897.4022 | 887.1699 | 876.9377 | 866.7054 | 856.4731 | 846.2408 | 836.0085 | 825.7763 | 815.544 | 805.3117

## CCCT
Source material |  |  |  | Adjustments
| Base | Percentage of total CAPEX | Scale to 2021 NREL 2019 vintage, 2019 $ | PSE Adjustment 1: escalate to 2020 $ | PSE Adjustment 1 Total | PSE Adjustment 2: add Spur Line | PSE Adjustment 2 Total | PSE ADJUSTED CAPITAL COST
NREL ATB Nameplate (MW) | 727
Description | $/kW | % of Total | $/kW | Multiplier | $/kW | Adder | $/kW | $/kW
Feedwater & Misc. BOP Systems | 129.5406 | 12.46% | 131.2666 | 2.5% | 134.5482 | 0 | 134.5482 | 134.5482
CT & Accessories | 156.4801 | 15.05% | 158.565 | 2.5% | 162.5291 | 0 | 162.5291 | 162.5291
HRSG, Ductwork & Stack | 158.5832 | 15.25% | 160.6962 | 2.5% | 164.7136 | 0 | 164.7136 | 164.7136
Steam Turbine & Accessories | 132.8377 | 12.77% | 134.6076 | 2.5% | 137.9728 | 0 | 137.9728 | 137.9728
Cooling Water System | 53.6561 | 5.16% | 54.371 | 2.5% | 55.7303 | 0 | 55.7303 | 55.7303
Accessory Electric Plant | 56.8542 | 5.468% | 57.6117 | 2.5% | 59.052 | 0 | 59.052 | 59.052
Instrumentation & Control | 26.8955 | 2.586% | 27.2538 | 2.5% | 27.9352 | 0 | 27.9352 | 27.9352
Improvements to Site | 38.2916 | 3.682% | 38.8018 | 2.5% | 39.7718 | 0 | 39.7718 | 39.7718
Building & Structure | 26.74 | 2.572% | 27.0963 | 2.5% | 27.7737 | 3.4388 | 31.2125 | 31.2125 | added 5mi spur line for interconnection assumed at $500,000 per mile
Total | 779.879 | 75% | 790.2699 | 2.5% | 810.0267 | 0 | 813.4655 | 813.4655
Owners Cost
Pre-Production Costs | 27.5598 | 2.65% | 27.927 | 2.5% | 28.6252 | 0 | 28.6252 | 28.6252
Inventory Capital | 4.3109 | 0.4146% | 4.3683 | 2.5% | 4.4775 | 0 | 4.4775 | 4.4775
Initial Cost for Catalyst & Chemicals | 1.1651 | 0.112% | 1.1806 | 2.5% | 1.2101 | 0 | 1.2101 | 1.2101
Land | 0.41265 | 0.03968% | 0.41815 | 2.5% | 0.42861 | 0 | 0.42861 | 0.42861
Other Owner's Costs | 116.9821 | 11.25% | 118.5408 | 2.5% | 121.5043 | 0 | 121.5043 | 121.5043
Financing Costs | 21.0564 | 2.025% | 21.3369 | 2.5% | 21.8704 | 0 | 21.8704 | 21.8704
Total Overnight Costs | 951.3659 | 91.49% | 964.0417 | 2.5% | 988.1428 | 0 | 991.5816 | 991.5816
TASC Multiplier (IOU, 33 year) | 1.093 | 1.093 | 1151.6915 | 1.093 | 1.093 | 1.093 | 1.093 | 1.093
Total As-Spent Cost | 1039.8429 | 100% | 1053.6976 | 2.5% | 1080.0401 | 0 | 1083.7987 | 1083.7987
↓ COST CURVE ↓
Year | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
NREL ATB Listing | 1053.6976 | 1049.3118 | 1043.8295 | 1041.6366 | 1029.5755 | 1025.1897 | 1025.1897 | 1020.8038 | 1012.0322 | 1007.6463 | 1003.2605 | 998.8746 | 995.5853 | 991.1994 | 984.6207 | 981.3313 | 976.9455 | 971.4632 | 967.0773 | 963.7879 | 959.4021 | 955.0163 | 950.6304 | 946.2446 | 942.9552 | 938.5694 | 935.28 | 931.9906 | 927.6048 | 922.1225 | 917.7366 | 906.772
% change on year | -- | 0.0041623 | 0.0052247 | 0.0021008 | 0.011579 | 0.0042599 | 0 | 0.0042781 | 0.0085929 | 0.0043337 | 0.0043526 | 0.0043716 | 0.0032931 | 0.0044053 | 0.0066372 | 0.0033408 | 0.0044693 | 0.0056117 | 0.0045147 | 0.0034014 | 0.0045506 | 0.0045714 | 0.0045924 | 0.0046136 | 0.0034762 | 0.0046512 | 0.0035047 | 0.003517 | 0.0047059 | 0.0059102 | 0.0047562 | 0.011947
After PSE Adjustments | 1083.7987 | 1079.2875 | 1073.6486 | 1071.3931 | 1058.9875 | 1054.4763 | 1054.4763 | 1049.9652 | 1040.9429 | 1036.4318 | 1031.9207 | 1027.4096 | 1024.0262 | 1019.5151 | 1012.7484 | 1009.365 | 1004.8539 | 999.215 | 994.7039 | 991.3205 | 986.8094 | 982.2983 | 977.7871 | 973.276 | 969.8927 | 965.3815 | 961.9982 | 958.6148 | 954.1037 | 948.4648 | 943.9537 | 932.6758

## Frame Peaker
Source material |  |  |  | Adjustments
| Base | Percentage of total CAPEX | Scale to 2021 NREL 2019 vintage, 2019 $ | PSE Adjustment 1: escalate to 2020 $ | PSE Adjustment 1 Total | PSE Adjustment 2: Add Fuel Storage Tank | PSE Adjustment 2 Total | PSE Adjustment 3: Add 5 Mile Spur Line | PSE Adjustment 3 Total | PSE ADJUSTED CAPITAL COST
NREL ATB Nameplate (MW) | 233
Cost Components | $, thousands | % of Total | $/kW | Multiplier | $/kW | Adder | $/kW | Adder | $/kW | $/kW
Civil/structural/architectural subtotal | 12300 | 7.419% | 69.47 | 2.5% | 71.2067 | -- | 71.2067 | -- | 71.2067 | 71.2067
Mech. Major equipment | 54000 | 32.57% | 304.9902 | 2.5% | 312.615 | -- | 312.615 | -- | 312.615 | 312.615
Mech. BOP | 17200 | 10.37% | 97.145 | 2.5% | 99.5737 | 64.3777 | 163.9513 | -- | 163.9513 | 163.9513 | add fuel oil (distillate or biodiesel) storage tank, assumed $15,000,000 for 24hrs of capacit
Mechanical subtotal | 71200 | 42.95% | 402.1353 | 2.5% | 412.1886 | -- | 412.1886 | -- | 412.1886 | 412.1886
Electrical subtotal | 20200 | 12.18% | 114.0889 | 2.5% | 116.9412 | -- | 116.9412 | -- | 116.9412 | 116.9412
Project indirects | 1900 | 1.146% | 10.7311 | 2.5% | 10.9994 | -- | 10.9994 | -- | 10.9994 | 10.9994
EPC fee | 12270 | 7.401% | 69.3006 | 2.5% | 71.0331 | -- | 71.0331 | -- | 71.0331 | 71.0331
EPC subtotal | 134970 | 81.41% | 762.3061 | 2.5% | 781.3638 | -- | 846.3204 | -- | 846.3204 | 846.3204
Owner's services | 9448 | 5.699% | 53.362 | 2.5% | 54.696 | -- | 54.696 | -- | 54.696 | 54.696
Land | 600 | 0.3619% | 3.3888 | 2.5% | 3.4735 | -- | 3.4735 | -- | 3.4735 | 3.4735
Electrical Interconnection | 1200 | 0.7238% | 6.7776 | 2.5% | 6.947 | -- | 6.947 | 10.7296 | 17.6766 | 17.6766 | added 5mi spur line for interconnection assumed at $500,000 per mile
Gas interconnection | 4500 | 2.714% | 25.4159 | 2.5% | 26.0512 | -- | 26.0512 | -- | 26.0512 | 26.0512
Owner's cost subtotal | 15748 | 9.499% | 88.9442 | 2.5% | 91.1678 | -- | 91.1678 | -- | 101.8974 | 101.8974
Project contingency | 15072 | 9.091% | 85.1262 | 2.5% | 87.2543 | -- | 87.2543 | -- | 87.2543 | 87.2543
Total CAPEX | 165790 | 100% | 936.3765 | 2.5% | 959.7859 | -- | 1024.7425 | -- | 1035.4721 | 1035.4721
↓ COST CURVE ↓
Year | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
NREL ATB Listing | 936.3765 | 927.6048 | 918.8331 | 914.4473 | 895.8074 | 885.9393 | 882.6499 | 876.0712 | 862.9137 | 856.3349 | 850.8526 | 846.4668 | 843.1774 | 837.6951 | 832.2128 | 827.827 | 823.4411 | 817.9588 | 813.573 | 809.1871 | 805.8978 | 800.4155 | 796.0296 | 791.6438 | 787.258 | 782.8721 | 779.5827 | 775.1969 | 770.8111 | 766.4252 | 760.9429 | 752.1712
% change on year | -- | 0.0093677 | 0.0094563 | 0.0047733 | 0.020384 | 0.011016 | 0.0037129 | 0.0074534 | 0.015019 | 0.0076239 | 0.006402 | 0.0051546 | 0.003886 | 0.006502 | 0.0065445 | 0.0052701 | 0.005298 | 0.0066578 | 0.0053619 | 0.0053908 | 0.004065 | 0.0068027 | 0.0054795 | 0.0055096 | 0.0055402 | 0.005571 | 0.0042017 | 0.0056259 | 0.0056577 | 0.0056899 | 0.0071531 | 0.011527
After PSE Adjustments | 1035.4721 | 1025.7721 | 1016.0721 | 1011.2221 | 990.6097 | 979.6972 | 976.0597 | 968.7848 | 954.2348 | 946.9598 | 940.8973 | 936.0474 | 932.4099 | 926.3474 | 920.2849 | 915.4349 | 910.5849 | 904.5224 | 899.6725 | 894.8225 | 891.185 | 885.1225 | 880.2725 | 875.4225 | 870.5725 | 865.7226 | 862.0851 | 857.2351 | 852.3851 | 847.5351 | 841.4726 | 831.7726

## Biomass
Source material |  |  |  | Adjustments
| Base | Percentage of total CAPEX | Scale to 2021 NREL 2019 vintage, 2019 $ | PSE Adjustment 1: escalate to 2020 $ | PSE Adjustment 1 Total | PSE Adjustment 2: Add 5 Mile Spur Line | PSE Adjustment 2 Total | PSE ADJUSTED CAPITAL COST
NREL ATB Nameplate (MW) | 50
Cost component | $ | % of Total | $/kW | Multiplier | $/kW | Adder | $/kW | $/kW
civil/structural/architectural | 22266000 | 10.87% | 472.3587 | 2.5% | 484.1677 | 0 | 484.1677 | 484.1677
Mechanical | 88818000 | 43.36% | 1884.216 | 2.5% | 1931.3214 | 0 | 1931.3214 | 1931.3214
Electrical | 26608000 | 12.99% | 564.4714 | 2.5% | 578.5832 | 0 | 578.5832 | 578.5832
Project indirects | 15418000 | 7.526% | 327.0828 | 2.5% | 335.2599 | 0 | 335.2599 | 335.2599
EPC fee | 15311000 | 7.474% | 324.8129 | 2.5% | 332.9332 | 0 | 332.9332 | 332.9332
EPC subtotal | 168421000 | 82.21% | 3572.9418 | 2.5% | 3662.2654 | 0 | 3662.2654 | 3662.2654
Owners costs
Owner's services | 11789000 | 5.755% | 250.096 | 2.5% | 256.3484 | 0 | 256.3484 | 256.3484
Land | 1500000 | 0.7322% | 31.8215 | 2.5% | 32.6171 | 0 | 32.6171 | 32.6171
Electrical Interconnection* | 1200000 | 0.5858% | 25.4572 | 2.5% | 26.0936 | 50 | 76.0936 | 76.0936 | added 5mi spur line for interconnection assumed at $500,000 per mile
Owners cost subtotal | 14489000 | 7.073% | 307.3747 | 2.5% | 315.0591 | 0 | 365.0591 | 365.0591
Contingency | 21949000 | 10.71% | 465.6337 | 2.5% | 477.2746 | 0 | 477.2746 | 477.2746
Total CAPEX | 204859000 | 100% | 4345.9502 | 2.5% | 4454.599 | 0 | 4504.599 | 4504.599
↓ COST CURVE ↓
Year | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
NREL ATB Listing ($/kW) | 4345.9502 | 4332.6652 | 4319.3801 | 4305.8828 | 4277.501 | 4275.1529 | 4275.1029 | 4252.9547 | 4231.7588 | 4209.2563 | 4184.795 | 4156.2735 | 4132.5081 | 4101.2522 | 4067.8429 | 4039.9838 | 4011.7541 | 3981.1082 | 3952.515 | 3925.3676 | 3899.5899 | 3871.2224 | 3840.15 | 3813.5155 | 3787.4884 | 3761.1822 | 3737.8896 | 3710.9765 | 3681.7677 | 3652.1007 | 3623.5845 | 3559.5324
% change on year | -- | 0.0030569 | 0.0030663 | 0.0031248 | 0.0065914 | 0.00054896 | 1.1688e-05 | 0.0051807 | 0.0049838 | 0.0053175 | 0.0058113 | 0.0068155 | 0.005718 | 0.0075634 | 0.0081461 | 0.0068486 | 0.0069876 | 0.007639 | 0.0071822 | 0.0068684 | 0.0065669 | 0.0072745 | 0.0080265 | 0.0069358 | 0.006825 | 0.0069456 | 0.0061929 | 0.0072001 | 0.0078709 | 0.0080578 | 0.0078082 | 0.017676
After PSE Adjustments ($/kW) | 4504.599 | 4490.829 | 4477.0589 | 4463.0689 | 4433.6511 | 4431.2172 | 4431.1654 | 4408.2087 | 4386.239 | 4362.915 | 4337.5608 | 4307.9981 | 4283.3651 | 4250.9683 | 4216.3394 | 4187.4632 | 4158.2031 | 4126.4384 | 4096.8015 | 4068.663 | 4041.9443 | 4012.5412 | 3980.3345 | 3952.7278 | 3925.7506 | 3898.484 | 3874.3411 | 3846.4455 | 3816.1705 | 3785.4206 | 3755.8633 | 3689.473

## Reference
Average Annual Inflation: | 2.5%

## Battery_Flow
Source material |  |  | Adjustments | [6 empty] | Source material |  |  |  | Adjustments | [6 empty] | Source material |  |  |  | Adjustments
| Base | Percentage of total CAPEX | scale to 2021 NREL 2019 vintage, 2019 $ | PSE Adjustment 1: escalate to 2020 $ | PSE Adjustment 1 Total | PSE Adjustment 2: Overbuild Storage Block | PSE Adjustment 2 Total | PSE ADJUSTED CAPITAL COST |  |  |  | Base | Percentage of total CAPEX | scale to 2021 NREL 2019 vintage, 2019 $ | PSE Adjustment 1: escalate to 2020 $ | PSE Adjustment 1 Total | PSE Adjustment 2: add Spur Line | PSE Adjustment 2 Total | PSE ADJUSTED CAPITAL COST |  |  |  | Base | Percentage of total CAPEX | scale to 2021 NREL 2019 vintage, 2019 $ | PSE Adjustment 1: escalate to 2020 $ | PSE Adjustment 1 Total | PSE Adjustment 2: add Spur Line | PSE Adjustment 2 Total | PSE ADJUSTED CAPITAL COST
NREL ATB Nameplate (MW) | 60 | [8 empty] | NREL ATB Nameplate (MW) |  | 60 | [8 empty] | NREL ATB Nameplate (MW) |  | 60
Duration (Hours) | 2 | [8 empty] | Duration (Hours) |  | 4 | [8 empty] | Duration (Hours) |  | 6
Lithium Ion Batteries | [9 empty] | Lithium Ion Batteries | [10 empty] | Lithium Ion Batteries
Duration | [9 empty] | Duration | [10 empty] | Duration
Module Component | $/kW | % of Total | $/kW | Multiplier | $/kW | Multiplier | $/kW | $/kW |  | Module Component |  | $/kW | % of Total | $/kW | Multiplier | $/kW | Multiplier | $/kW | $/kW |  | Module Component |  | $/kW | % of Total | $/kW | Multiplier | $/kW | Multiplier | $/kW | $/kW
Storage Block | 696 | 48.4% | 413.079 | 2.5% | 423.406 | 20% | 508.0872 | 508.0872 |  | Storage Block |  | 1044 | 50.46% | 723.7285 | 2.5% | 741.8217 | 20% | 890.186 | 890.186 |  | Storage Block |  | 1392 | 51.37% | 1035.0686 | 2.5% | 1060.9453 | 20% | 1273.1344 | 1273.1344
Storage balance of system | 140 | 9.736% | 83.0906 | 2.5% | 85.1679 | -- | 85.1679 | 85.1679 |  | Storage balance of system |  | 208 | 10.05% | 144.1911 | 2.5% | 147.7959 | -- | 147.7959 | 147.7959 |  | Storage balance of system |  | 276 | 10.18% | 205.2291 | 2.5% | 210.3598 | -- | 210.3598 | 210.3598
Power Equipment | 115 | 7.997% | 68.253 | 2.5% | 69.9593 | -- | 69.9593 | 69.9593 |  | Power Equipment |  | 115 | 5.558% | 79.721 | 2.5% | 81.7141 | -- | 81.7141 | 81.7141 |  | Power Equipment |  | 115 | 4.244% | 85.5121 | 2.5% | 87.6499 | -- | 87.6499 | 87.6499
Controls & communication | 2 | 0.1391% | 1.187 | 2.5% | 1.2167 | -- | 1.2167 | 1.2167 |  | Controls & communication |  | 2 | 0.09667% | 1.3865 | 2.5% | 1.4211 | -- | 1.4211 | 1.4211 |  | Controls & communication |  | 2 | 0.0738% | 1.4872 | 2.5% | 1.5243 | -- | 1.5243 | 1.5243
System integration | 132 | 9.179% | 78.3426 | 2.5% | 80.3011 | -- | 80.3011 | 80.3011 |  | System integration |  | 192 | 9.28% | 133.0995 | 2.5% | 136.427 | -- | 136.427 | 136.427 |  | System integration |  | 168 | 6.199% | 124.9221 | 2.5% | 128.0451 | -- | 128.0451 | 128.0451
Eng., procurement, construction | 152 | 10.57% | 90.2127 | 2.5% | 92.468 | -- | 92.468 | 92.468 |  | Eng., procurement, construction |  | 216 | 10.44% | 149.7369 | 2.5% | 153.4803 | -- | 153.4803 | 153.4803 |  | Eng., procurement, construction |  | 192 | 7.085% | 142.7681 | 2.5% | 146.3373 | -- | 146.3373 | 146.3373
Project Dev | 184 | 12.8% | 109.2048 | 2.5% | 111.9349 | -- | 111.9349 | 111.9349 |  | Project Dev |  | 272 | 13.15% | 188.5576 | 2.5% | 193.2715 | -- | 193.2715 | 193.2715 |  | Project Dev |  | 240 | 8.856% | 178.4601 | 2.5% | 182.9216 | -- | 182.9216 | 182.9216
Grid integration | 20 | 1.391% | 11.8701 | 2.5% | 12.1668 | -- | 12.1668 | 12.1668 |  | Grid integration |  | 20 | 0.9667% | 13.8645 | 2.5% | 14.2111 | -- | 14.2111 | 14.2111 |  | Grid integration |  | 20 | 0.738% | 14.8717 | 2.5% | 15.2435 | -- | 15.2435 | 15.2435
Total ESS intalled cost | 1438 | 100% | 853.4592 | 2.5% | 874.7957 | -- | 961.3019 | 961.3019 |  | Total ESS intalled cost |  | 2069 | 100% | 1434.2856 | 2.5% | 1470.1427 | -- | 1618.5071 | 1618.5071 |  | Total ESS intalled cost |  | 2710 | 100% | 2015.112 | 2.5% | 1833.0269 | -- | 2045.216 | 2045.216
↓ COST CURVES ↓
2hr LI
Year | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
NREL ATB Listing | 853.4592 | 810.0348 | 763.3964 | 716.7579 | 670.1194 | 623.4809 | 576.8425 | 559.5765 | 542.3105 | 525.0444 | 507.7784 | 490.5124 | 485.2256 | 479.9387 | 474.6518 | 469.3649 | 464.078 | 458.7911 | 453.5043 | 448.2174 | 442.9305 | 437.6436 | 432.3567 | 427.0698 | 421.783 | 416.4961 | 411.2092 | 405.9223 | 400.6354 | 395.3485 | 390.0617 | 384.7748
% change on year | -- | 0.05088 | 0.057576 | 0.061093 | 0.065069 | 0.069597 | 0.074803 | 0.029932 | 0.030855 | 0.031838 | 0.032885 | 0.034003 | 0.010778 | 0.010896 | 0.011016 | 0.011138 | 0.011264 | 0.011392 | 0.011524 | 0.011658 | 0.011795 | 0.011936 | 0.01208 | 0.012228 | 0.012379 | 0.012535 | 0.012694 | 0.012857 | 0.013024 | 0.013196 | 0.013373 | 0.013554
After PSE Adjustments |  | 1010.2133 | 961.3019 | 902.5727 | 843.8435 | 785.1143 | 726.3851 | 704.643 | 682.9009 | 661.1588 | 639.4167 | 617.6746 | 611.0171 | 604.3597 | 597.7022 | 591.0447 | 584.3872 | 577.7298 | 571.0723 | 564.4148 | 557.7573 | 551.0999 | 544.4424 | 537.7849 | 531.1274 | 524.47 | 517.8125 | 511.155 | 504.4975 | 497.8401 | 491.1826 | 484.5251
4hr LI
Year | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
NREL ATB Listing | 1434.2856 | 1363.2842 | 1281.8131 | 1200.3419 | 1118.8707 | 1037.3996 | 955.9284 | 921.5615 | 887.1946 | 852.8276 | 818.4607 | 784.0938 | 774.2926 | 764.4915 | 754.6903 | 744.8891 | 735.088 | 725.2868 | 715.4856 | 705.6844 | 695.8833 | 686.0821 | 676.2809 | 666.4797 | 656.6786 | 646.8774 | 637.0762 | 627.2751 | 617.4739 | 607.6727 | 597.8715 | 588.0704
% change on year | -- | 0.049503 | 0.059761 | 0.063559 | 0.067873 | 0.072816 | 0.078534 | 0.035951 | 0.037292 | 0.038737 | 0.040298 | 0.04199 | 0.0125 | 0.012658 | 0.012821 | 0.012987 | 0.013158 | 0.013333 | 0.013514 | 0.013699 | 0.013889 | 0.014085 | 0.014286 | 0.014493 | 0.014706 | 0.014925 | 0.015152 | 0.015385 | 0.015625 | 0.015873 | 0.016129 | 0.016393
After PSE Adjustments |  | 1698.6279 | 1618.5071 | 1515.6359 | 1412.7646 | 1309.8934 | 1207.0222 | 1163.6281 | 1120.2341 | 1076.84 | 1033.4459 | 990.0518 | 977.6762 | 965.3006 | 952.9249 | 940.5493 | 928.1736 | 915.798 | 903.4223 | 891.0467 | 878.671 | 866.2954 | 853.9197 | 841.5441 | 829.1684 | 816.7928 | 804.4171 | 792.0415 | 779.6658 | 767.2902 | 754.9145 | 742.5389
6hr LI
Year | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
NREL ATB Listing | 2015.112 | 1916.5336 | 1800.2298 | 1683.9259 | 1567.622 | 1451.3182 | 1335.0143 | 1283.5465 | 1232.0787 | 1180.6108 | 1129.143 | 1077.6752 | 1063.3597 | 1049.0443 | 1034.7288 | 1020.4134 | 1006.0979 | 991.7824 | 977.467 | 963.1515 | 948.836 | 934.5206 | 920.2051 | 905.8897 | 891.5742 | 877.2587 | 862.9433 | 848.6278 | 834.3123 | 819.9969 | 805.6814 | 791.366
% change on year | -- | 0.04892 | 0.060684 | 0.064605 | 0.069067 | 0.074191 | 0.080137 | 0.038552 | 0.040098 | 0.041773 | 0.043594 | 0.045581 | 0.013284 | 0.013462 | 0.013646 | 0.013835 | 0.014029 | 0.014229 | 0.014434 | 0.014645 | 0.014863 | 0.015087 | 0.015319 | 0.015557 | 0.015803 | 0.016056 | 0.016318 | 0.016589 | 0.016869 | 0.017158 | 0.017458 | 0.017768
After PSE Adjustments |  | 2145.267 | 2045.216 | 1913.0848 | 1780.9536 | 1648.8224 | 1516.6912 | 1458.2193 | 1399.7474 | 1341.2756 | 1282.8037 | 1224.3318 | 1208.0682 | 1191.8046 | 1175.541 | 1159.2774 | 1143.0138 | 1126.7502 | 1110.4866 | 1094.223 | 1077.9594 | 1061.6958 | 1045.4322 | 1029.1686 | 1012.905 | 996.6414 | 980.3778 | 964.1142 | 947.8506 | 931.5871 | 915.3235 | 899.0599
WORK IN PROGRESS

## Pumped Storage Hydro
Source material |  |  |  | Adjustments
| Base | Percentage of total CAPEX | scale to 2021 NREL 2019 vintage, 2019 $ | PSE Adjustment 1: add Spur Line | PSE Adjustment 1 Total | PSE ADJUSTED CAPITAL COST
NREL ATB Nameplate (MW) | 500
Hours | 10
Cost component | $/kW | % of Total | $/kW | Adder | $/kW | $/kW
Upper + lower reservoir | 1016 | 31.69% | 841.75 | -- | 841.75 | 841.75
Tunnels | 163 | 5.084% | 135.0445 | -- | 135.0445 | 135.0445
Powerhouse excavation | 97 | 3.026% | 80.3639 | -- | 80.3639 | 80.3639
Powerhouse structure, equip. BOP | 1010 | 31.5% | 836.779 | 5 | 841.779 | 841.779
Total direct costs | 2286 | 71.3% | 1893.9375 | -- | 1898.9375 | 1898.9375
EPC management services inc. contingency | 472 | 14.72% | 391.0492 | -- | 391.0492 | 391.0492
Owner's cost | 448 | 13.97% | 371.1654 | -- | 371.1654 | 371.1654
Proj mgmt & design engineering | 103 | 3.213% | 85.3349 | -- | 85.3349 | 85.3349
Construction mgmt & startup support | 103 | 3.213% | 85.3349 | -- | 85.3349 | 85.3349
contingency | 308 | 9.607% | 255.1762 | -- | 255.1762 | 255.1762
Total indirect cost | 920 | 28.7% | 762.2146 | -- | 762.2146 | 762.2146
Total installed cost | 3206 | 100% | 2656.152 | -- | 2661.152 | 2661.152
↓ COST CURVE ↓
Year | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
NREL ATB Listing** | 2656.152 | 2656.152 | 2656.152 | 2656.152 | 2656.152 | 2656.152 | 2656.152 | 2656.152 | 2656.152 | 2656.152 | 2656.152 | 2656.152 | 2656.152 | 2656.152 | 2656.152 | 2656.152 | 2656.152 | 2656.152 | 2656.152 | 2656.152 | 2656.152 | 2656.152 | 2656.152 | 2656.152 | 2656.152 | 2656.152 | 2656.152 | 2656.152 | 2656.152 | 2656.152 | 2656.152 | 2656.152
% change on year | -- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
After PSE Adjustments |  | 2661.152 | 2661.152 | 2661.152 | 2661.152 | 2661.152 | 2661.152 | 2661.152 | 2661.152 | 2661.152 | 2661.152 | 2661.152 | 2661.152 | 2661.152 | 2661.152 | 2661.152 | 2661.152 | 2661.152 | 2661.152 | 2661.152 | 2661.152 | 2661.152 | 2661.152 | 2661.152 | 2661.152 | 2661.152 | 2661.152 | 2661.152 | 2661.152 | 2661.152 | 2661.152 | 2661.152
WORK IN PROGRESS

## Recip Peaker
Source material |  |  |  | Adjustments
| Base | Percentage of total CAPEX | scale to 2021 NREL 2019 vintage, 2019 $ | PSE Adjustment 1: escalate to 2020 $ | PSE Adjustment 1 Total | PSE Adjustment 2: | PSE Adjustment 2 Total | PSE ADJUSTED CAPITAL COST
NREL ATB Nameplate (MW) | 21.4
Cost Components | $, thousands | % of Total | $/kW | Multiplier | $/kW | Adder | $/kW | $/kW
Civil/structural/architectural subtotal | 6861 | 17.72% | 296.0871 | 2.5% | 303.4893 | -- | 303.4893 | 303.4893
Engines | 11974 | 30.92% | 516.7392 | 2.5% | 529.6576 | -- | 529.6576 | 529.6576
Mechanical BOP | 5521 | 14.26% | 238.2593 | 2.5% | 244.2158 | -- | 244.2158 | 244.2158
Mechanical subtotal | 17495 | 45.18% | 754.9985 | 2.5% | 773.8734 | -- | 773.8734 | 773.8734
Electrical subtotal | 6668 | 17.22% | 287.7582 | 2.5% | 294.9522 | -- | 294.9522 | 294.9522
Project indirects | 180 | 0.4648% | 7.7679 | 2.5% | 7.9621 | -- | 7.9621 | 7.9621
EPC fee | 1923 | 4.966% | 82.9873 | 2.5% | 85.0619 | -- | 85.0619 | 85.0619
EPC subtotal | 33127 | 85.54% | 1429.599 | 2.5% | 1465.3389 | -- | 1465.3389 | 1465.3389
Owner's services | 1586 | 4.095% | 68.444 | 2.5% | 70.1551 | -- | 70.1551 | 70.1551
Land | 300 | 0.7747% | 12.9465 | 2.5% | 13.2702 | -- | 13.2702 | 13.2702
Owner's fuirnished equipment |  |  | 0
Electrical Interconnection | 720 | 1.859% | 31.0717 | 2.5% | 31.8485 | 127.3939 | 159.2423 | 159.2423
Gas interconnection | 125 | 0.3228% | 5.3944 | 2.5% | 5.5292 | -- | 5.5292 | 5.5292
Owner's cost subtotal | 14705 | 37.97% | 634.5957 | 2.5% | 650.4606 | -- | 650.4606 | 650.4606
Project contingency | 2869 | 7.408% | 123.812 | 2.5% | 126.9073 | -- | 126.9073 | 126.9073
Total CAPEX | 38727 | 100% | 1671.2675 | 2.5% | 1713.0492 | -- | 1840.443 | 1840.443
↓ COST CURVE ↓
Year | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
NREL ATB Listing** | 1671.2675 | 1683.3252 | 1670.7683 | 1637.8359 | 1622.6008 | 1613.5505 | 1604.593 | 1595.506 | 1588.5778 | 1578.4239 | 1572.7785 | 1567.6519 | 1560.4722 | 1554.9924 | 1549.969 | 1543.9632 | 1538.0373 | 1532.9563 | 1529.8743 | 1525.9768 | 1522.2711 | 1520.1345 | 1514.5698 | 1513.2246 | 1507.9839 | 1506.3061 | 1501.6543 | 1498.4012 | 1495.1241 | 1491.7136 | 1476.832 | 637.6301
% change on year | -- | -0.0072147 | 0.0074596 | 0.019711 | 0.009302 | 0.0055777 | 0.0055514 | 0.0056631 | 0.0043423 | 0.0063918 | 0.0035766 | 0.0032596 | 0.0045799 | 0.0035116 | 0.0032305 | 0.0038748 | 0.0038381 | 0.0033036 | 0.0020105 | 0.0025476 | 0.0024284 | 0.0014036 | 0.0036606 | 0.00088817 | 0.0034633 | 0.0011126 | 0.0030882 | 0.0021663 | 0.0021871 | 0.0022811 | 0.0099762 | 0.56824
After PSE Adjustments |  | 1827.1648 | 1840.443 | 1804.1662 | 1787.3839 | 1777.4145 | 1767.5473 | 1757.5376 | 1749.9057 | 1738.7207 | 1732.5019 | 1726.8547 | 1718.9458 | 1712.9096 | 1707.376 | 1700.7603 | 1694.2326 | 1688.6356 | 1685.2406 | 1680.9473 | 1676.8653 | 1674.5116 | 1668.3819 | 1666.9001 | 1661.1271 | 1659.279 | 1654.1547 | 1650.5713 | 1646.9613 | 1643.2044 | 1626.8116 | 702.3845
WORK IN PROGRESS

## Small Modular Nuclear
Source material |  |  | Adjustments
| Base | Percentage of total CAPEX | PSE Adjustment 1: convert to $/kW | PSE Adjustment 1 Total | PSE Adjustment 2: escalate to 2020 $ | PSE Adjustment 2 Total | PSE Adjustment 3: Add 5 Mile Spur Line | PSE Adjustment 3 Total | PSE ADJUSTED CAPITAL COST
NREL ATB Nameplate (MW) | 600 |  | Divisor | $/kW | Multiplier | $/kW | Adder | $/kW | $/kW
Civil/structural/architectural subtotal | 583524 | 15.71% | 600 | 972.54 | 1.97% | 991.699 | -- | 991.699 | 991.699
Nuclear island | 648360 | 17.45% | 600 | 1080.6 | 1.97% | 1101.8878 | -- | 1101.8878 | 1101.8878
Conventional island | 421434 | 11.35% | 600 | 702.39 | 1.97% | 716.2271 | -- | 716.2271 | 716.2271
Balance of Plant | 389016 | 10.47% | 600 | 648.36 | 1.97% | 661.1327 | -- | 661.1327 | 661.1327
Mechanical subtotal | 1458810 | 39.27% | 600 | 2431.35 | 1.97% | 2479.2476 | -- | 2479.2476 | 2479.2476
Electrical subtotal | 259344 | 6.982% | 600 | 432.24 | 1.97% | 440.7551 | -- | 440.7551 | 440.7551
Project indirects | 551000 | 14.83% | 600 | 918.3333 | 1.97% | 936.4245 |  | 936.4245 | 936.4245
EPC fee | 285267.8 | 7.68% | 600 | 475.4463 | 1.97% | 484.8126 | -- | 484.8126 | 484.8126
EPC subtotal | 3137945.8 | 84.48% | 600 | 5229.9097 | 1.97% | 5332.9389 | -- | 5332.9389 | 5332.9389
Owner's services | 235346 | 6.336% | 600 | 392.2433 | 1.97% | 399.9705 |  | 399.9705 | 399.9705
Land | 1050 | 0.02827% | 600 | 1.75 | 1.97% | 1.7845 | -- | 1.7845 | 1.7845
Electrical Interconnection | 2520 | 0.06784% | 600 | 4.2 | 1.97% | 4.2827 | 16.8 | 21.0827 | 21.0827
Owner's cost subtotal | 238916 | 6.432% | 600 | 398.1933 | 1.97% | 406.0377 | -- | 422.8377 | 422.8377
Project contingency | 337686 | 9.091% | 600 | 562.81 | 1.97% | 573.8974 |  | 573.8974 | 573.8974
Total CAPEX | 3714547.8 | 100% | 600 | 6190.913 | 1.97% | 6312.874 |  | 6329.674 | 6329.674
Not enough information available to generate reliable cost curve at present
WORK IN PROGRESS

## Electrolyzer
WORK IN PROGRESS