## Project Path
How do I know if my project is a controls project versus EBCx, MBCx, HVAC Capital, O&M, or P4P?
HVAC Controls (this Excel worksheet) is suitable if you are adding or improving sequences of operation and ensuring that all sequences meet the 2021 Washington State Energy Code (WSEC) Requirements (in section C403). New controls hardware is typically included but not required. A base incentive correlated to 3-5% annual building consumption is paid upon project completion and verification. There is a 1-year performance period, with a performance incentive paid if final savings exceed base savings.
Existing Building Commissioning (EBCx) is suitable if you are going through a whole-building Cx process with plans to implement the < 2-year payback measures identified. An assessment incentive is paid upon initial investigation/walk-through of the building to identify opportunities. A $/sqft implementation incentive is paid upon implementation of the measures, delivery of the final investigation report and all verification documentation. There is a 1-year performance period, with a performance incentive paid if final savings exceed 6% of annual metered consumption. This may identify new or improved sequences of operations without requiring all sequences being brought up to code; however, if a full controls upgrade is identified and warranted, PSE can transition the project to HVAC Controls.
Monitoring-Based Commissioning (MBCx) is suitable if you are implementing a technological path for an ongoing commissioning process by deploying an FDD software application to continually monitor, identify, and fix issues with the building's operation. This may include adds/improves to isolated sequences of operations without requiring all sequences being brought up to code. A $/sqft implementation incentive is paid upon project completion and once all verification documentation is provided. There are two 1-year performance periods, each with a performance incentive paid if final savings exceed 6% of annual metered consumption.
HVAC Capital Upgrade is suitable if you are adding HVAC hardware and/or controls function but are not bringing all sequences up to code. Qualifying measures are funded at $0.45/kWh and $8/Therm, up to 70% of the cost. Do not use this HVAC Controls Worksheet. Instead, note the project details on a PSE custom grant application. The project will be analyzed using one of the following two options: A custom-calculated option is available for measures which can have savings calculated reliably (e.g. DCV, fan VFD). The incentive is paid upon project completion and verification. There is no performance incentive. A performance-only option is available for measures with at least 3% estimated annual metered savings. The incentive is paid after a 1-year performance period if the savings meet or exceed 3%. There is no base incentive.
HVAC Operations & Maintenance (O&M) is suitable if you are tuning and/or fixing existing hardware and/or functions but are not utilizing a formal assessment or approved implementer, and you are not bringing all sequences up to code. Qualifying measures are funded at $0.10/kWh and $2/Therm, up to 100% of the cost. Do not use this HVAC Controls Worksheet. Instead, note the project details on a PSE custom grant application. The project will be analyzed using one of the following two options: A custom-calculated option is available for O&M measures which can have savings calculated reliably (e.g. lighting and/or basic HVAC schedule adjustments). The incentive is paid upon project completion and verification. There is no performance incentive. A performance-only option is available for measures with at least 3% estimated annual metered savings. The incentive is paid after a 1-year performance period if the savings meet or exceed 3%. There is no base incentive.
Pay for Performance (P4P) is suitable if you are pursuing at least two capital measures (one of which can be HVAC controls) to be installed within a 12-month period with anticipated site savings over 15% (or 10% if PSE gas only). An implementation incentive correlated to 5% annual building consumption is paid upon project completion and verification. There are two 1-year performance periods, each with a performance incentive paid if final savings exceed previously claimed savings.

## Instructions
HVAC Controls Process Steps for the Contractor or Controls Project Lead | Process Steps for PSE
Setting Up the Grant | Setting Up the Grant
1. If all controls are being brought up to code, proceed to step 2. Otherwise submit a custom grant application or schedule a scope review. | 1. Conduct Scope Review meeting with the contractor and review the submitted Worksheet page if one has been submitted.
2. Obtain signed data release form from the customer for all affected accounts. | 2. Request additional site info to confirm the values on the Worksheet tab. Collect OA docs. If OA is < 80% of code, contact controls SME.
3. Ensure that you are using the most recent version of the Worksheet by downloading it from the PSE webpage. | 3. Email the customer and contractor the Base + Performance Incentive table from the Worksheet tab for the grant estimate.
4. Fill out the Worksheet tab, inputting information into all green cells and explaining any added or improved sequences. | 4. With the go-ahead to proceed, create the QC packet. Use SoW template on PSE Only - DSMc Inputs tab.
5. Schedule Scope Review meeting with PSE to go over the project and determine the most likely incentive pathway (Commissioning@pse.com) | 5. When the draft Sequences of Operation are provided, notify contractor of any necessary edits to comply with code.
6. If moving forward, submit a PSE Grant Application.
7. Document existing conditions on the OA Calibration tab (or use your own document). | Paying the Base Grant
8. Work with the assigned PSE Energy Management Engineer to answer any other questions and execute the grant agreement. | 1. Receive the final invoices, sequences of operation, Facility Guide, and trends from the contractor.
9. Send PSE a draft of the Sequences of Operation to ensure compliance with code requirements. | 2. Review the submitted information and confirm that the requirements for each sequence is met.
3. Assemble a partial payment request for the base grant.
Getting the Base Grant Paid | 4. Mark your Outlook calendar for 6 months and 12 months after the date when the controls were fully commissioned for the mid-year savings
Send the following to PSE: | check-in and final performance analysis, respectively.
1. Final invoices
2. Facility Guide document | Paying the Performance Grant
1. Perform a mid-year check-in at the 6 month mark to see savings trends and allow time for correction if needed.
Getting the Performance Grant Paid | 2. When one year since the project was fully commissioned has passed, determine any building changes that occurred.
1. Wait for 1 year to pass after the project is complete and fully commissioned. | 3. Perform a savings analysis using a PSE regression tool.
2. Notify PSE of any changes to the building you are aware of (occupancy, space use type, major equipment changes, etc). | 4. If savings are much lower than expected (<base), contact a PSE Controls SME.
3. PSE will provide a calculation of savings using billing data, and will provide the associated performance incentive amount. | 5. If savings are reasonable (>base), notify the customer and contractor of the final savings and associated performance grant amount.
4. Review the final incentive amount with the customer and give PSE approval to proceed with the performance grant payment. | 6. With customer/contractor approval, submit the final performance payment request for QC review regardless of size.
*Note For All* - Updates to this worksheet can be made by PSE at any time. We will do our best to inform you of major updates, but it is your responsibility to use the correct version.
For the most recent version, please contact PSE or visit https://www.pse.com/en/business-incentives/hvac-incentive-and-rebate-programs/major-hvac-controls-upgrade-rebates

## Worksheet
2026 PSE HVAC Controls Worksheet v1.0
Project Name |  |  |  | Add or Improve? | non-Central Plant Sequences | Link to 2021 WA State Energy Code | Explain all Adds and Improves below
Address |  |  |  | N/A or Meets Code | Zone level scheduling & limited time override - C403.4.1 & C403.4.2.2 |  | Example Add: OA dampers stay open and electric reheat is currently used during building warm-up. Adding Automated Start/Stop will shut OA dampers and prioritize pre-heat.
Scope Review | Incomplete - Contact PSE when Ready |  |  | N/A or Meets Code | Automated start/stop for warm-up and for cool-down - C403.4.2.3
Building Type |  |  |  | N/A or Meets Code | Thermostatic Setback - C403.4.2.1
Project Type |  | Will all sequences meet code? | Select | N/A or Meets Code | Supply air temperature (SAT) reset - C403.6.4 |  | Example Improve: Replacing existing economizer controls while implementing fault detection.
Building Sq Ft |  |  |  | N/A or Meets Code | Duct static pressure (DSP) reset based on load - C403.6.8
Controls Cost |  |  |  | N/A or Meets Code | Demand controlled ventilation (DCV) with single zone system - C403.7.1
PSE Project Cost | 0 |  |  | N/A or Meets Code | Upgrade to VFD (from inlet vane or from constant volume) - C403.2.4
PSE Usage Data |  |  |  | N/A or Meets Code | Zone box air & temperature controls - C403.6.1
|  |  |  | N/A or Meets Code | Air-side economizer controls (integrated, FDD) - C403.5.1
Annual Gas Usage |  | therms/yr |  | N/A or Meets Code | Room space temperatures setpoints deadband - C403.4.1.2
|  |  |  | N/A or Meets Code | HEAT PUMPS ONLY: Heat pump strip heating control - C403.4.1.1
Annual Elec Usage |  | kWh/yr |  | N/A or Meets Code | LABS ONLY: Exhaust and OA ventilation reduction - C403.7.7.2
Clean Buildings Law EUI Target (EUIt) |  |  | kBTU/sqft/yr |  | Central Plant Sequences - worth half points
Total Building EUI |  |  | kBTU/sqft/yr | N/A or Meets Code | WSHP loop temperature setpoints deadband - C403.4.3.3
|  |  |  | N/A or Meets Code | Differential pressure control for building loop pump(s) >10 hp - C403.4.3.3.3
Major Process Loads >5% of Building Use |  |  |  | N/A or Meets Code | Efficient cooling tower operation - C403.4.3.3.2 & C403.9.1.4
Load Type | kWh/yr or Therms/yr | UOM | Description | N/A or Meets Code | Condenser water temperature (CWT) reset based on load
Data Center |  |  |  | N/A or Meets Code | Chilled water temperature (CHWT) reset based on load - C403.4.4
Large DHW |  |  |  | N/A or Meets Code | Hot water temperature (HWT) reset based on load - C403.4.4
Refrigeration |  |  |  | N/A or Meets Code | Boiler and chiller plant lockout on OA temperature
Pool |  |  |  | N/A or Meets Code | Efficient boiler modulation and staging - C403.4.3
Base Incentive |  |  |  |  | Other Sequences - worth half points
| Measure Cost | Base Savings | Base Incentive | N/A or Meets Code | VAV temp & ventilation setback based on occupancy - C403.6.5 & C403.6.6 |  | *PSE will determine which sequences qualify
Electric | 0 | 0 | 0 | N/A or Meets Code | Analytics - AI and/or Fault Detection & Diagnostics - C403.2.3
Gas | 0 | 0 | 0 | N/A or Meets Code | DCV for multi-zone spaces (with PSE approval) - C403.7.1 |  | Explain other upcoming bldg changes or projects below
Totals | 0 |  | 0 | N/A or Meets Code | Door contacts/switches for mechanical system shut off - C403.4.1.6
|  |  |  | N/A or Meets Code | Water-side economizer for chilled water plant - C403.5.4
Performance Incentive (Finalized after Performance Period) |  |  |  | N/A or Meets Code | Valves to isolate plant or HP equipment from loop when not in use - C403.4.3.3
| Gross Site Savings | Perf Savings | Perf Incentive* | N/A or Meets Code | Efficient Loop Pump Control - C403.4.6
Electric | 0 | 0 | Unqualified | N/A or Meets Code | Multi-zone VAV Ventilation Optimization Control - C403.6.5
Gas | 0 | 0 | Unqualified | N/A or Meets Code | Cooling Tower Fan Speed Control - C403.9.1.1
Totals |  |  | 0 | N/A or Meets Code | Other (with PSE approval)
*Only finalized after 12 months post-install* |  |  |  | N/A or Meets Code | Other (with PSE approval) |  | 0 | Adds
*Site must exceed base savings to be eligible for a performance incentive* |  |  |  | 0 | Total points |  | 0 | Improves
|  |  |  | 0% | Base Savings | Point Structure | ACKNOWLEDGEMENT Users of this file acknowledge that there are no incentive guarantees until PSE has thoroughly reviewed the proposed changes and provided a grant agreement.
Total Base + Performance Incentive Estimates | [5 empty] | 0 - 0.9 Points = 0% base savings
|  | Final savings % | Total Incentive | OA Baseline Recorded? |  | 1 - 1.9 Points = 3% base savings
This section estimates your total incentive award (base + performance) after the 12-month performance period with various site savings percentages |  | 0% or less | 0 | No | Required Before Grant | 2 - 2.9 points = 4% base savings
|  | 10% | Unqualified |  |  | 3+ points = 5% base savings
|  | 15% | Unqualified | Facility Guide Requirements Here
|  | 25% | Unqualified
Initial Grant
Final True-up*
Note on C16: Overwrite this value for multi-type buildings.
Note on B34: Only change this number after the performance period
Note on B35: Only change this number after the performance period

## OA Calibration
Project Name: |  | 0 | [8 empty] | Date(s) of existing measurements: | [7 empty] | Date(s) of final measurements:
Outside Air Calibration Documentation - Offered as a courtesy but you may use your own document
Fill in green cells in chart - expand rows to capture all AHUs (HPs, FCUs, RTUs, AHUs).
Document the existing condition. Determine the code requirement. Balance and document the final DDC OA% needed to meet code.
Temperature calculation method can only be used if OAT, RAT and MAT accurately reflect these temperatures and there is a 20 F difference between OAT and RAT
|  | Required Before Grant Agreement | [14 empty] | Required After Project Completion
|  | EXISTING MIN OA |  |  |  |  | ASHRAE 62.1 MIN OA REQUIREMENT | [9 empty] | FINAL BALANCED MIN OA
|  | DDC | MEASURED WHEN OA AT MIN (HEATING MODE) |  |  |  | Area |  |  | Non-People Code |  | People Code |  | TOTAL CODE MIN |  |  | MEASURED WHEN OA AT MIN (HEATING MODE)* |  |  |  | Calculated OAT* | Measured | DDC
EQUIP# | Building | Min OA% stpt | MAT | RAT | OAT | Existing OA% | Type | People density/ 1000 sf | sf | cfm/sf | Code Min OA Cfm | cfm/ person | Code Min OA Cfm | Code Total cfm | Total AHU cfm | Code OA% | MAT | RAT | OAT | Traverse cfm | Final OA% | Traverse OA% | Min OA% stpt
HP-Example | 34 | 15% | 66 | 70 | 40 | 13.33% | Game arcades | 20 | 1500 | 0.18 | 270 | 7.5 | 225 | 495 | 1500 | 33% | 64 | 70 | 40 | 250 | 20% | 16.67% | 15%
[10 empty] | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0
Q=mCpdeltaT (1.08*CFM*deltaT) using OSA bin calc, add to baseline

## Facility Guide
The Facility Guide shall include the following:
1. Outline of the Guide
2. Written Description of Systems and Operation
a. HVAC overview
b. Sequence of Operations
i. Annotated Trends Showing Proper Added/Improved Sequence Operation
c. Ventilation amount and control with completed Outside Air Calibration document (or equivalent)
i. If VAV boxes or controls replaced, provide k-factor flow coefficients
d. How systems (e.g. AHU & VAV boxes) are zoned and how the zones are controlled
e. Key items to monitor to maintain efficiency. (e.g. schedules, ventilation, setpoints, calibration of OA and CO2)
f. Unique challenges of building (e.g. high solar gain, OSA sensors not agreeing, comfort complaints, indoor air quality)
4. Training Provided – who, what and when - emphasis on GUI navigation proficiency

## Energy Code
2021 Washington State Energy Code Sequence Sections
Zone level scheduling & limited time override
C403.4.1 Thermostatic controls. The supply of heating and cooling energy to each zone shall be controlled
by individual thermostatic controls capable of responding to temperature within the zone. Controls in the same
zone or in neighboring zones connected by openings larger than 10 percent of the floor area of either zone
shall not allow for simultaneous heating and cooling. At a minimum, each floor of a building shall be
considered as a separate zone. Controls on systems required to have economizers and serving single zones
shall have multiple cooling stage capability and activate the economizer when appropriate as the first stage of
cooling. See Section C403.5 for further economizer requirements. Where humidification or dehumidification or
both is provided, at least one humidity control device shall be provided for each humidity control system.
C403.4.2.2 Automatic setback and shutdown. Automatic time clock or programmable controls shall be
capable of starting and stopping the system for seven different daily schedules per week and retaining their
programming and time setting during a loss of power for at least 10 hours. Additionally, the controls shall
have a manual override that allows temporary operation of the system for up to 2 hours; a manually
operated timer configured to operate the system for up to 2 hours; or an occupancy sensor.
Automated Start and Stop
C403.4.2.3 Automatic start and stop. Automatic start and stop controls shall be provided for each HVAC
system. The automatic start controls shall be configured to automatically adjust the daily start time of the
HVAC system in order to bring each space to the desired occupied temperature immediately prior to
scheduled occupancy. Automated stop controls shall be provided for each HVAC system with direct digital
control of individual zones. The automatic stop controls shall be configured to reduce the HVAC system’s
heating temperature set point and increase the cooling temperature set point by at least 2°F (1.1°C) before
scheduled unoccupied periods based upon the thermal lag and acceptable drift in space temperature that is
within comfort limits.
Thermostatic Setback
C403.4.2.1 Thermostatic setback. Thermostatic setback controls shall be configured to set back or
temporarily operate the system to maintain zone temperatures down to 55°F (13°C) or up to 85°F (29°C).
Supply-air temperature reset
C403.6.4 Supply-air temperature reset controls. Multiple zone HVAC systems shall include controls that
are capable of and configured to automatically reset the supply-air temperature in response to representative
building loads, or to outdoor air temperature. The controls shall be configured to reset the supply air
temperature at least 25 percent of the difference between the design supply-air temperature and the design
room air temperature. Controls that adjust the reset based on zone humidity are allowed. HVAC zones that
are expected to experience relatively constant loads shall have maximum airflow designed to accommodate
the fully reset supply air temperature.
Exceptions:
1. Systems that prevent reheating, recooling or mixing of heated and cooled supply air.
2. Seventy-five percent (75%) of the energy for reheating is from a site-recovered source.
Duct Static Pressure Reset Based on Load
C403.6.8 Set points for direct digital control. For systems with direct digital control of individual zones
reporting to the central control panel, the static pressure set point shall be reset based on the zone requiring
the most pressure. In such cases, the set point is reset lower until one zone damper is nearly wide open. The
direct digital controls shall be capable of monitoring zone damper positions or shall have an alternative
method of indicating the need for static pressure that is configured to provide all of the following:
1. Automatically detecting any zone that excessively drives the reset logic.
2. Generating an alarm to the system operational location.
3. Allowing an operator to readily remove one or more zones from the reset algorithm.
Demand Control Ventilation
C403.7.1 Demand control ventilation.
C403.7.1.1 Spaces requiring demand control ventilation. Demand control ventilation (DCV) shall be
provided for the following:
1. Spaces with ventilation provided by single-zone systems where an air economizer is provided to
comply with Section C403.5.
2. Spaces with an occupant load greater than or equal to 15 people per 1000 square feet (93 m2) of floor
area (as established in Table 403.3.1.1 of the International Mechanical Code) or with an occupant
outdoor airflow rate greater than or equal to 15 cfm/person, as established in Table 403.3.1.1 of the
International Mechanical Code.
Exceptions:
1. Spaces including, but not limited to, dining areas, where more than 75 percent of the space design
outdoor airflow is transfer air required for makeup air supplying an adjacent commercial kitchen.
2. Spaces with one of the following occupancy classifications as defined in Table 403.3.1.1 of the
International Mechanical Code: Correctional cells, educational laboratories, barbers, beauty and nail
salons, and bowling alley seating.
3. Dormitory sleeping areas with fewer than five occupants per space.
4. Spaces with ventilation not provided by a single-zone system where the design occupant component
outdoor airflow is less than 100 cfm (23.6 L/s), or 200 cfm (47.2 L/s) with system having energy
recovery with minimum 60 percent sensible effectiveness. Design occupant component outdoor
airflow shall be calculated as the product of the design number of occupants in the space and the
people outdoor airflow rate per occupant (Rp) as established in Table 403.3.1.1 of the International
Mechanical Code.
5. Spaces with ventilation not provided by a single-zone system where the total system design outdoor
airflow is less than 750 cfm (354 L/s), or 1500 cfm (708 L/s) with system having energy recovery with
minimum 60 percent sensible effectiveness.
C403.7.1.2 Demand control ventilation design. Each space required to have demand control ventilation
shall have equipment and controls capable of and configured to automatically change the quantity of
outdoor air supplied to the space based upon the output of a CO2 sensor. System outdoor air intake shall be
adjusted from peak design levels in response to changes in outdoor air required in the spaces served by the
system. This adjustment shall be accomplished by variable speed fan control.
Exception: These system types may use other means of adjusting outdoor air:
1. Single zone systems designed to recirculate return air.
2. Systems with total supply air less than 1500 cfm (708 L/s).
Upgrade to VFD
C403.2.4 Variable flow capacity. For fan and pump motors 5.0 hp and greater including motors in or
serving custom and packaged air handlers serving variable air volume fan systems, constant volume fans,
heating and cooling hydronic pumping systems, pool and service water pumping systems, domestic water
pressure-booster systems, cooling tower fan, and other pump or fan motors where variable flows are
required, there shall be:
1. Variable speed drives; or
2. Other controls and devices that will result in fan and pump motor demand of no more than 30 percent of
design wattage at 50 percent of design air volume for fans when static pressure set point equals 1/3 the
total design static pressure, and 50 percent of design water flow for pumps, based on manufacturer's
certified test data. Variable inlet vanes, throttling valves (dampers), scroll dampers or bypass circuits
shall not be allowed.
Exception: Variable speed devices are not required for motors that serve:
1. Fans or pumps in packaged equipment where variable speed drives are not available as a factory
option from the equipment manufacturer.
2. Fans or pumps that are required to operate only for emergency fire-life-safety events (e.g., stairwell
pressurization fans, elevator pressurization fans, fire pumps, etc.).
Zone Box Air & Temp Controls
C403.6.1 Variable air volume (VAV) and multiple zone systems. Supply air systems serving multiple zones
shall be VAV systems that have zone controls configured to reduce the volume of air that is reheated,
recooled or mixed in each zone to one of the following:
1. Twenty percent of the zone design peak supply for systems with direct digital control (DDC) and thirty
percent of the maximum supply air for other systems.
2. Systems with DDC where items 2.1 through 2.3 apply.
2.1 The airflow rate in the dead band between heating and cooling does not exceed 20 percent of the
zone design peak supply rate or higher allowed rates under items 3, 4 or 5 of this section.
2.2 The first stage of heating modulates the zone supply air temperature set point up to a maximum set
point while the airflow is maintained at the dead band flow rate.
2.3 The second stage of heating modulates the airflow rate from the dead band flow rate up to the
heating maximum flow rate that is less than 50 percent of the zone design peak supply rate.
3. The outdoor airflow rate required to meet the minimum ventilation requirements of Chapter 4 of the
International Mechanical Code.
4. Any higher rate that can be demonstrated to reduce overall system annual energy use by offsetting
reheat/recool energy losses through a reduction in outdoor air intake for the system as approved by the
code official.
5. The airflow rate required to comply with applicable codes or accreditation standards such as pressure
relationships or minimum air change rates.
Exception: The following individual zones or entire air distribution systems are exempted from the
requirement for VAV control:
1. Zones or supply air systems where not less than 75 percent of the energy for reheating or for
providing warm air in mixing systems is provided from a site-recovered source, including
condenser heat.
2. Systems that prevent reheating, recooling, mixing or simultaneous supply of air that has been
previously cooled, either mechanically or through the use of economizer systems, and air that has
been previously mechanically heated.
3. .Ventilation systems complying with Section C403.3.5, DOAS, with ventilation rates complying
with Section C403.2.2.
Air-side Economizer Controls
C403.5.1 Integrated economizer control. Economizer systems shall be integrated with the mechanical
cooling system and be configured to provide partial cooling even where additional mechanical cooling is
required to provide the remainder of the cooling load. Controls shall not be capable of creating a false load in
the mechanical cooling system by limiting or disabling the economizer or any other means, such as hot gas
bypass, except at the lowest stage of mechanical cooling.
Units that include an air economizer shall comply with the following:
1. Unit controls shall have the mechanical cooling capacity control interlocked with the air economizer
controls such that the outdoor air damper is at the 100 percent open position when mechanical
cooling is on and the outdoor air damper does not begin to close to prevent coil freezing due to
minimum compressor run time until the leaving air temperature is less than 45°F (7°C).
2. Direct expansion (DX) units with cooling capacity 65,000 Btu/H (19 kW) or greater of rated capacity
shall comply with the following:
2.1. DX units that control the capacity of the mechanical cooling directly based on occupied space
temperature shall have not fewer than two stages of mechanical cooling capacity.
2.2. Other DX units, including those that control space temperature by modulating the airflow to the
space, shall be in accordance with Table C403.5.1.
C403.5.3.2 Control signal. Economizer controls and dampers shall be configured to sequence the dampers
with mechanical cooling equipment and shall not be controlled by only mixed air temperature. Air
economizers on systems with cooling capacity greater than 65,000 Btu/h shall be configured to provide
partial cooling even when additional mechanical cooling is required to meet the remainder of the cooling
load.
Exception: The use of mixed air temperature limit control shall be permitted for systems that are both
controlled from space temperature (such as single zone systems) and having cooling capacity less than
65,000 Btu/h.
C403.5.3.3 High-limit shutoff. Air economizers shall be configured to automatically reduce outdoor air
intake to the design minimum outdoor air quantity when outdoor air intake will no longer reduce cooling
energy usage. High-limit shutoff control types shall be chosen from Table C403.5.3.3. High-limit shutoff
control settings for these control types shall be those specified in Table C403.5.3.3.
C403.5.5 Economizer fault detection and diagnostics (FDD). Air-cooled unitary direct-expansion units with
a cooling capacity of 54,000 Btu/h or greater listed in the tables in Section C403.3.2 that are equipped with an
economizer in accordance with Section C403.5 shall include a fault detection and diagnostics (FDD) system
complying with the following:
1. The following temperature sensors shall be permanently installed to monitor system operation:
1.1. Outside air.
1.2. Supply air.
1.3. Return air.
2. Temperature sensors shall have an accuracy of ±2°F (1.1°C) over the range of 40°F to 80°F (4°C to
26.7°C).
3. Refrigerant pressure sensors, where used, shall have an accuracy of ±3 percent of full scale.
4. The unit controller shall be configured to provide system status by indicating the following:
4.1. Free cooling available.
4.2. Economizer enabled.
4.3. Compressor enabled.
4.4. Heating enabled.
4.5. Mixed air low limit cycle active.
4.6. The current value of each sensor.
5. The unit controller shall be capable of manually initiating each operating mode so that the operation of
compressors, economizers, fans and the heating system can be independently tested and verified.
6. The unit shall be configured to report faults to a fault management application available for access by
day-to-day operating or service personnel or annunciated locally on zone thermostats.
7. The FDD system shall be configured to detect the following faults:
7.1. Air temperature sensor failure/fault.
7.2. Not economizing when the unit should be economizing.
7.3. Economizing when the unit should not be economizing.
7.4. Damper not modulating.
7.5. Excess outdoor air.
Room Space Temp Setpoints Deadband
C403.4.1.2 Deadband. Where used to control both heating and cooling, zone thermostatic controls shall be
configured to provide a temperature range or dead band of at least 5°F (2.8°C) within which the supply of
heating and cooling energy to the zone is shut off or reduced to a minimum.
Exceptions:
1. Thermostats requiring manual changeover between heating and cooling modes.
2. Occupancies or applications requiring precision in indoor temperature control as approved by the
code official.
Heat Pump Strip Heating Control
C403.4.1.1 Heat pump supplementary heat control. Heat pumps equipped with internal electric
resistance heaters shall have controls that prevent supplemental heater operation when the heating load
can be met by the heat pump alone during both steady-state operation and setback recovery. Supplemental
heart operation is permitted during outdoor coil defrost cycles. Heat pumps equipped with supplemental
heaters shall comply with all conditions of Section C403.1.4.
Exceptions:
1. Packaged terminal heat pumps (PTHPs) of less than 2 tons (24,000 Btu/hr) cooling capacity and
whose ratings meet the requirements shown in Table C403.3.2(4) that have reverse-cycle demand
defrost and are configured to operate in heat pump mode whenever the outdoor air temperatures
are above 25°F
(-3.9°C) and the unit is not in defrost.
2. Heat pumps whose minimum efficiency is regulated by NAECA and whose ratings meet the
requirements shown in Table C403.3.2(2) and include all usage of internal electric resistance
heating.
Lab Exhaust and OA Ventilation Reduction
C403.7.7.2 Laboratory exhaust systems. Buildings with laboratory exhaust systems having a total exhaust
rate greater than 5,000 cfm (2,360 L/s) shall include heat recovery systems to preconditioned replacement
air from laboratory exhaust. The heat recovery system shall be capable of increasing the outside air supply
temperature at design heating conditions by 25°F (13.9°C). A provision shall be made to bypass or control
the heat recovery system to permit air economizer operation as required by Section C403.5.
Exceptions:
1. Variable air volume laboratory exhaust and room supply systems configured to reduce exhaust
and make-up air volume to 50% or less of design values; or
2. Direct make-up (auxiliary) air supply equal to at least 75% of the exhaust rate, heated no warmer
than 2°F (1.1°C) below room set point, cooled to no cooler than 3°F (1.7°C) above room set point,
no humidification added, and no simultaneous heating and cooling used for dehumidification
control; or
3. Combined energy reduction method: VAV exhaust and room supply system configured to reduce
exhaust and makeup air volumes and a heat recovery system to precondition makeup air from
laboratory exhaust that when combined will produce the same energy reduction as achieved by a
heat recovery system with a 50% sensible recovery effectiveness as required above. For
calculation purposes, the heat recovery component can be assumed to include the maximum
design supply airflow rate at design conditions. The combined energy reduction (QER) shall meet
the following:
QER ≥ QMIN
QMIN = CFMS x (TR - TO) x 1.1 x 0.6
QER = CFMS x (TR - TO) x 1.1(A+B)/100
Where:
QMIN = Energy recovery at 60% sensible effectiveness (Btu/h)
QER = Combined energy reduction (Btu/h)
CFMS = The maximum design supply airflow rate to conditioned spaces served by the
system in cubic feet per minute
TR = Space return air dry bulb at winter design conditions
TO = Outdoor air dry bulb at winter design conditions
A = Percentage that the exhaust and makeup air volumes can be reduced from design
conditions
B = Percentage sensible heat recovery effectiveness
WSHP Loop Temp Setpoints Deadband
C403.4.3.3.1 Temperature dead band. Hydronic heat pumps connected to a common heat pump water
loop with central devices for heat rejection and heat addition shall have controls that are configured to
provide a heat pump water supply temperature dead band of at least 20°F (11.1°C) between initiation of
heat rejection and heat addition by the central devices.
Exception: Where a system loop temperature optimization controller is installed and can determine the
most efficient operating temperature based on real time conditions of demand and capacity, dead bands
of less than 20°F (11°C) shall be permitted.
Differential pressure control for building loop pump(s) >10 hp
C403.4.3.3.3 Isolation valve. Each hydronic heat pump on the hydronic system having a total pump
system power exceeding 10 horsepower (hp) (7.5 kW) shall have a two-way (but not three-way) valve. For
the purposes of this section, pump system power is the sum of the nominal power demand (i.e.,
nameplate horsepower at nominal motor efficiency) of motors of all pumps that are required to operate at
design conditions to supply fluid from the heating or cooling source to all heat transfer devices (e.g., coils,
heat exchanger) and return it to the source. This converts the system into a variable flow system and, as
such, the primary circulation pumps shall comply with the variable flow requirements in Section C403.4.6.
Efficient Cooling Tower Operation
C403.4.3.3.2 Heat rejection. The following shall apply to hydronic water loop heat pump systems:
1. Where a closed-circuit cooling tower is used directly in the heat pump loop, either an automatic
valve shall be installed to bypass the flow of water around the closed-circuit cooling tower, except
for the minimum flow necessary for freeze protection. Flow controls for freeze protection shall not
allow water through the closed-circuit cooling tower when outdoor temperatures are above the
freezing point of the glycol/water solution, i.e. 32°F (0°C) for 100 percent water applications, and
18°F (-7.8°C) for 20 percent by mass propylene glycol solution.
2. Where an open-circuit cooling tower is used directly in the heat pump loop, an automatic valve shall
be installed to bypass all heat pump water flow around the open-circuit cooling tower.
3. Where an open-circuit cooling tower is used in conjunction with a separate heat exchanger to
isolate the open-circuit cooling tower from the heat pump loop, heat loss shall be controlled by
shutting down the circulation pump on the cooling tower loop.
Exception: Where it can be demonstrated that a heat pump system will be required to reject heat
throughout the year.
C403.9.1.4 Tower flow turndown. Open-circuit cooling towers used on water-cooled chiller systems that are
configured with multiple- or variable-speed condenser water pumps shall be designed so that all open circuit
cooling tower cells can be run in parallel with the larger of the flow that is produced by the smallest pump at its
minimum expected flow rate or at 50 percent of the design flow for the cell.
Condenser Water Temperature Reset - No Code Section
If OA < 55F, Condenser water setpoint = 70F
If OA > 85F, Condenser water setpoint = 85F
Linear reset between 55F and 85F OA temp.
10 minute time delay before responding to OA temp changes.
The contractor may deviate from these values based on the building.
Chilled Water Temperature Reset & Hot Water Temperature Reset
C403.4.4 Part load controls. Hydronic systems greater than or equal to 300,000 Btu/h (88 kW) in design
output capacity supplying heated or chilled water to comfort conditioning systems shall include controls that
are configured to:
1. Automatically reset the supply-water temperatures in response to varying building heating and cooling
demand using coil valve position, zone-return water temperature or outdoor air temperature. The
temperature shall be reset by not less than 25 percent of the design supply-to-return water temperature
difference.
Exceptions:
1. Hydronic systems serving hydronic heat pumps.
2. Hydronic systems with thermal energy storage where resetting the supply-water temperature
would reduce the capacity of the storage.
2. Automatically vary fluid flow for hydronic systems with a combined pump motor capacity of 2 hp or
larger with three or more control valves or other devices by reducing the system design flow rate by not
less than 50 percent or the maximum reduction allowed by the equipment manufacturer for proper
operation of equipment by valves that modulate or step open and close, or pumps that modulate or turn
on and off as a function of load.
3. Automatically vary pump flow on heating water systems, chilled-water systems and heat rejection loops
serving water-cooled unitary air conditioners as follows:
3.1. Where pumps operate continuously or operate based on a time schedule, pumps with nominal
output motor power of 2 hp or more shall have a variable speed drive.
3.2. Where pumps have automatic direct digital control configured to operate pumps only when zone
heating or cooling is required, a variable speed drive shall be provided for pumps with motors
having the same or greater nominal output power indicated in Table C403.4.4 based on the climate
zone and system served.
4. Where a variable speed drive is required by Item 3 of this Section, pump motor power input shall be
not more than 30 percent of design wattage at 50 percent of the design water flow. Pump flow shall be
controlled to maintain one control valve nearly wide open or to satisfy the minimum differential
pressure.
Exceptions:
1. Supply-water temperature reset is not required for chilled-water systems supplied by off-site district
chilled water or chilled water from ice storage systems.
2. Variable pump flow is not required on dedicated coil circulation pumps where needed for freeze
protection.
3. Variable pump flow is not required on dedicated equipment circulation pumps where configured in
primary/secondary design to provide the minimum flow requirements of the equipment manufacturer
for proper operation of equipment.
4. Variable speed drives are not required on heating water pumps where more than 50 percent of
annual heat is generated by an electric boiler.
Boiler and Chiller Plant Lockout on OA Temperature - No Code Section
Chiller Plant Lockout Logic
Disable chiller plant when outdoor air temperature falls below 55°F for 30 minutes.
Enable chiller plant when outdoor air temperature rises above 65°F for 15 minutes.
During lockout period, maximize economizer operation for cooling.
Maintain condenser water circulation if required for equipment protection.
Boiler Plant Lockout Logic
Disable boiler plant when outdoor air temperature rises above 75°F for 30 minutes.
Enable boiler plant when outdoor air temperature falls below 65°F for 15 minutes.
During lockout period, heating coils remain available but without hot water supply.
Maintain minimum circulation if required for freeze protection.
Contractor may deviate from these values based on the building.
Efficient Boiler Modulation and Staging
C403.4.3 Hydronic systems controls. The heating of fluids that have been previously mechanically cooled
and the cooling of fluids that have been previously mechanically heated shall be limited in accordance with
Sections C403.4.3.1 through C403.4.3.3. Hydronic heating systems comprised of multiple-packaged boilers
and designed to deliver conditioned water or steam into a common distribution system shall include automatic
controls configured to sequence operation of the boilers. Hydronic heating systems comprised of a single
boiler and greater than 500,000 Btu/h (146,550 W) input design capacity shall include either a multi-staged or
modulating burner.
VAV Temp and Ventilation Setback
C403.6.5 Multiple-zone VAV system ventilation optimization control. Multiple-zone VAV systems with
direct digital control of individual zone boxes reporting to a central control panel shall have automatic controls
configured to reduce outdoor air intake flow below design rates in response to changes in system ventilation
efficiency (Ev) as defined by the International Mechanical Code.
Exceptions:
1. VAV systems with zonal transfer fans that recirculate air from other zones without directly mixing it
with outdoor air, dual-duct dual-fan VAV systems, and VAV systems with fan-powered terminal units.
2. Systems where total design exhaust airflow is more than 70 percent of total design outdoor air intake
flow requirements.
C403.6.6 Parallel-flow fan-powered VAV air terminal control. Parallel-flow fan-powered VAV air terminals
shall have automatic controls configured to:
1. Turn off the terminal fan except when space heating is required or where required for ventilation.
2. Turn on the terminal fan as the first stage of heating before the heating coil is activated.
3. During heating for warmup or setback temperature control, either:
3.1. Operate the terminal fan and heating coil without primary air.
3.2. Reverse the terminal damper logic and provide heating from the central air handler by primary air.
AI and/or Fault Detection and Diagnostics
C403.2.3 Fault detection and diagnostics. New buildings with an HVAC system serving a gross
conditioned floor area of 100,000 square feet (9290 m2) or larger shall include a fault detection and
diagnostics (FDD) system to monitor the HVAC system’s performance and automatically identify faults. The
FDD system shall:
1. Include permanently installed sensors and devices to monitor the HVAC system’s performance.
2. Sample the HVAC system’s performance at least once every 15 minutes.
3. Automatically identify and report HVAC system faults.
4. Automatically notify authorized personnel of identified HVAC system faults.
5. Automatically provide prioritized recommendations for repair of identified faults based on analysis of
data collected from the sampling of HVAC system performance.
6. Be capable of transmitting the prioritized fault repair recommendations to remotely located authorized
personnel.
Door Contacts/Switches for Mechanical System Shutoff
C403.4.1.6 Operable opening switches for HVAC system thermostatic control. Operable openings
meeting the minimum size criteria of Section C402.5.11 and that open to the outdoors from a conditioned
space must have controls configured to do the following once doors have been open for 5 minutes:
1. Disable the mechanical heating to the zone or reset the space heating temperature set point to 55 °F
or less within 5 minutes of the door open enable signal.
2. Disable the mechanical cooling to the zone or reset the space cooling temperature set point to 85 °F
or more within 5 minutes of the door open enable signal.
Exception: Hydronic radiant heating and cooling systems.
Water-side Economizers
C403.5.4.1 Design capacity. Water economizer systems shall be configured to cool supply air by indirect
evaporation and providing up to 100 percent of the expected system cooling load at outdoor air
temperatures of not greater than 50°F dry-bulb (10°C dry-bulb)/45°F wet-bulb (7.2°C wet-bulb.
Exception: Systems where dehumidification requirements cannot be met using outdoor air temperatures
of 50°F dry-bulb (10°C dry-bulb)/45°F wet-bulb (7.2°C wet-bulb) and where 100 percent of the expected
system cooling load at 45°F dry-bulb (7.2°C dry-bulb)/40°F wet-bulb (4.5°C wet-bulb) is met with
evaporative water economizers.
C403.5.4.2 Maximum pressure drop. Precooling coils and water-to-water heat exchangers used as part of
a water economizer system shall either have a water-side pressure drop of less than 15 feet (4572 mm) of
water or a secondary loop shall be created so that the coil or heat exchanger pressure drop is not seen by
the circulating pumps when the system is in the normal cooling (noneconomizer) mode.
Valves to Isolate Plant or HP Equipment from Pumping Loop'
C403.4.3.3.2 Heat rejection. The following shall apply to hydronic water loop heat pump systems:
1. Where a closed-circuit cooling tower is used directly in the heat pump loop, either an automatic
valve shall be installed to bypass the flow of water around the closed-circuit cooling tower, except
for the minimum flow necessary for freeze protection. Flow controls for freeze protection shall not
allow water through the closed-circuit cooling tower when outdoor temperatures are above the
freezing point of the glycol/water solution, i.e. 32°F (0°C) for 100 percent water applications, and
18°F (-7.8°C) for 20 percent by mass propylene glycol solution.
2. Where an open-circuit cooling tower is used directly in the heat pump loop, an automatic valve shall
be installed to bypass all heat pump water flow around the open-circuit cooling tower.
3. Where an open-circuit cooling tower is used in conjunction with a separate heat exchanger to
isolate the open-circuit cooling tower from the heat pump loop, heat loss shall be controlled by
shutting down the circulation pump on the cooling tower loop.
Exception: Where it can be demonstrated that a heat pump system will be required to reject heat
throughout the year.
C403.4.3.3.3 Isolation valve. Each hydronic heat pump on the hydronic system having a total pump
system power exceeding 10 horsepower (hp) (7.5 kW) shall have a two-way (but not three-way) valve. For
the purposes of this section, pump system power is the sum of the nominal power demand (i.e.,
nameplate horsepower at nominal motor efficiency) of motors of all pumps that are required to operate at
design conditions to supply fluid from the heating or cooling source to all heat transfer devices (e.g., coils,
heat exchanger) and return it to the source. This converts the system into a variable flow system and, as
such, the primary circulation pumps shall comply with the variable flow requirements in Section C403.4.6.
Efficient Loop Pump Control
C403.4.6 Variable flow controls. Individual pumps required by this code to have variable speed control shall
be controlled in one of the following manners:
1. For systems having a combined pump motor horsepower less than or equal to 20 hp (15 kW) and
without direct digital control of individual coils, pump speed shall be a function of either:
1.1. Required differential pressure; or
1.2. Reset directly based on zone hydronic demand, or other zone load indicators; or
1.3. Reset directly based on pump power and pump differential pressure; or
1.4. Reset directly by an integral controller based on the relationship between variable speed
controller frequency and power.
2. For systems having a combined pump motor horsepower that exceeds 20 hp (15 kW) or smaller
systems with direct digital control, pump speed shall be a function of either:
2.1. The static pressure set point as reset based on the valve requiring the most pressure; or
2.2. Directly controlled based on zone hydronic demand; or
2.3. Reset directly by an integral controller based on the relationship between variable speed
controller frequency and power.
VAV Ventilation Optimization Control
C403.6.5 Multiple-zone VAV system ventilation optimization control. Multiple-zone VAV systems with
direct digital control of individual zone boxes reporting to a central control panel shall have automatic controls
configured to reduce outdoor air intake flow below design rates in response to changes in system ventilation
efficiency (Ev) as defined by the International Mechanical Code.
Exceptions:
1. VAV systems with zonal transfer fans that recirculate air from other zones without directly mixing it
with outdoor air, dual-duct dual-fan VAV systems, and VAV systems with fan-powered terminal units.
2. Systems where total design exhaust airflow is more than 70 percent of total design outdoor air intake
flow requirements.
Cooling Tower Fan Speed Control
C403.9.1.1 Fan speed control. Each fan powered by an individual motor or array of motors with a connected
power, including the motor service factor, totaling 5 hp (3.7 kW) or more shall have controls and devices
configured to automatically modulate the fan speed to control the leaving fluid temperature or condensing
temperature and pressure of the heat rejection device. Fan motor power input shall be not more than 30
percent of design wattage at 50 percent of the design airflow.
Exceptions:
1. Fans serving multiple refrigerant or fluid cooling circuits.
2. Condenser fans serving flooded condensers.

## Trends
Suggested Key Points to Trend | The trend points provided below are not a firm requirement. They are meant to be a starting point and general reference for sequence verification.
Zone-level Scheduling |  | Annotated Trend Example
Mode (occ, unocc, stand-by, warmup/cooldown)
Room Occupancy Status
Room temp cooling setpoint
Room temp heating setpoint
Room temp
Optimum Start/Stop
Outside Air Damper %
Gas burner command
Electric reheat command
Room temp cooling setpoint
Room temp heating setpoint
Room temp
Cooling valve %
Heating valve %
Unoccupied setback w/zone override
Mode (occ, unocc, stand-by, warmup/cooldown)
Room Occupancy Status
Room temp cooling setpoint
Room temp heating setpoint
Room temp
Outside Air Damper %
Electric Reheat Command
Supply Air Temp Reset
Supply Air Temperature
Supply Air Temperature Setpoint
Outside Air Temperature
Room temp cooling setpoint
Room temp heating setpoint
Room temp
Duct Static Pressure Reset
Duct Static Pressure (actual)
Duct Static Pressure Setpoint
Duct Static Pressure Demand (reset variable - typically VAV damper positions)
Supply Fan VFD %
Outside Air Temperature (if OAT reset)
Zone damper positions (sample 15% of VAV boxes)
Minimum Outside Air Ventilation with Positive Building Pressure Maintained
Outside Air Damper %
Building Pressure (actual)
Building Pressure Setpoint
Relief/Exhaust Fan VFD % or command
Supply Fan VFD %
Mixed Air Temperature
Outside Air Temperature
Return Air Temperature
Occupancy status (if variable OA based on occupancy)
Demand Control Ventilation (DCV) in Interior Spaces
CO2 levels (sample of representative zones)
CO2 setpoints
Outside Air Damper %
Occupancy status/override
Zone airflow (CFM) where applicable
Mixed Air Temperature
Mode (occupied/unoccupied/standby)
Zone/Box Air and Temperature Controls
Zone/Box CFM (actual)
Zone/Box CFM setpoint
VAV damper position %
Discharge Air Temperature (if available)
Space Temperature (actual)
Space Temperature Setpoint (heating & cooling)
Heating valve/reheat command %
Zone fan command (if applicable)
Mode (occupied/unoccupied/standby)
Occupancy override status
Upgrade to VFD on Supply Fan
Supply Fan VFD % (speed)
Supply Fan VFD command vs. feedback
Duct Static Pressure
Duct Static Pressure Setpoint
Motor amperage (if available)
Supply Air Temperature
Air-side Economizer Controls
Outside Air Temperature
Return Air Temperature
Mixed Air Temperature
Outside Air Damper %
Cooling valve % (mechanical cooling)
Supply Air Temperature
Supply Air Temperature Setpoint
Enthalpy (if enthalpy-based economizer)
Outside Humidity (if enthalpy-based)
Return Humidity (if enthalpy-based)
Economizer enable/lockout status
Room Space Temperature Setpoints Deadband
Space Temperature (actual)
Heating Setpoint
Cooling Setpoint
Deadband width (calculated or direct)
Mode (occupied/unoccupied/standby)
Heating command/valve %
Cooling command/valve %
Occupancy override status
Zone CFM (if VAV)
Central Plant Sequences
WSHP Loop Temperature Setpoints Deadband and Maximums
Building Loop Supply Temperature (actual)
Building Loop Return Temperature (actual)
Building Loop Heating Temperature Setpoint
Building Loop Cooling Temperature Setpoint
Deadband width (calculated or direct)
Maximum Loop Temperature Limit
Minimum Loop Temperature Limit
Loop Temperature Reset Variable (load demand)
Outside Air Temperature
Building heating/cooling demand
Differential Pressure (DP) Control for Building Loop Pump(s) >10 hp
HW/CHW Pump Differential Pressure (actual)
HW/CHW Pump Differential Pressure Setpoint
Load/Demand variable (determining DP reset setpoint)
Building HW/CHW loop pump speed %
Building HW/CHW loop pump status/command
Building loop supply temperature
Building loop return temperature
System flow rate (if available)
Pump motor amperage (if available)
Efficient Cooling Tower and Chiller Staging
Chiller #1, #2, #3 (etc.) command/status
Chiller #1, #2, #3 (etc.) % load or kW
Cooling Tower Fan #1, #2, #3 (etc.) command/speed %
Condenser Water Supply Temperature
Condenser Water Return Temperature
Chilled Water Supply Temperature
Chilled Water Return Temperature
Building cooling demand/load
Outside Air Temperature
Outside Air Humidity (wet bulb)
Lead/lag status indicators
Equipment runtime hours
Condenser Water Temperature (CWT) Reset Based on Load
Condensing Water Temperature (leaving) - actual
Condensing Water Temperature Setpoint
Controlling variable used to determine CW temp reset
Entering Water Temperature
Cooling Tower Fan command or speed %
Chiller % load or demand
Outside Air Temperature
Outside Air Humidity (wet bulb)
Approach temperature (calculated)
Chilled Water Temperature (CHWT) Reset Based on Load
Chiller Supply Water Temperature (actual)
Chiller Supply Water Temperature Setpoint
Building cooling demand (reset variable - not OAT)
CHW building loop supply temperature
CHW building loop return temperature
CHW building loop temperature setpoint
Chiller command/status
Building CHW loop pump speed %
Outside Air Temperature (for comparison/verification)
Zone cooling demands (sample of critical zones)
Hot Water Temperature (HWT) Reset Based on Load
Boiler HW Supply Temperature (actual)
Boiler HW Setpoint
Building heating demand (reset variable - not OAT)
HW building loop supply temperature
HW building loop return temperature
HW building loop temperature setpoint
Boiler command/status
Building HW loop pump speed %
Outside Air Temperature (for comparison/verification)
Zone heating demands (sample of critical zones)
Boiler and Chiller Plant Lockout on Outside Air Temperature (OAT)
Outside Air Temperature
Boiler lockout setpoint
Chiller lockout setpoint
Boiler command/status
Chiller command/status
Lockout override status (if applicable)
Building heating demand
Building cooling demand
Manual override status
Equipment availability status
Efficient Boiler Modulation and Staging
Boiler #1, #2, #3 (etc.) command/status
Boiler #1, #2, #3 (etc.) firing rate % or modulation %
Boiler #1, #2, #3 (etc.) supply temperature
Building heating demand/load
HW building loop supply temperature
HW building loop return temperature
HW building loop temperature setpoint
Lead/lag status indicators
Equipment runtime hours
Boiler efficiency % (if available)
Stack temperature (if available)
Other Sequences
VAV Setback Based on Occupancy
Zone occupancy status (occupied/unoccupied/override)
Zone CFM (actual)
Zone CFM setpoint (occupied vs. unoccupied)
VAV damper position %
Space temperature setpoint (occupied vs. unoccupied)
Space temperature (actual)
Occupancy override timer/duration
Motion sensor status (if applicable)
Schedule override status
Mode (occupied/unoccupied/standby)
Sample 15% of VAV boxes or minimum 3 per scheduling zone
Fault Detection and Diagnostics
Fault alarm status/active alarms
Filter differential pressure (if monitored)
Motor amperage vs. expected values
Temperature sensor readings vs. expected ranges
Damper/valve position feedback vs. command
VFD fault codes/status
Communication failures/timeouts
Sensor calibration drift indicators
Performance degradation indicators
Multi-Zone Demand-Controlled Ventilation
Zone CO2 levels (all DCV zones)
Zone CO2 setpoints
Zone occupancy counts/status
Outside Air Damper % (AHU level)
Zone airflow CFM (where applicable)
Mixed Air Temperature
Outside Air Temperature
Door Switches On/Off Contact
Door position status (open/closed)
Door open duration timer
Associated equipment lockout status
Space temperature during door events
Door cycle frequency
Related HVAC equipment response
Override timer status
Manual bypass status
Interlock alarm status
Water-Side Economizer for Chiller Plant
Outside Air Temperature (wet bulb)
Cooling Tower Water Supply Temperature
Chilled Water Supply Temperature
Chilled Water Return Temperature
Water-side economizer valve position %
Chiller bypass valve position %
Cooling tower fan speed %
Building cooling load/demand
Water-side economizer enable/disable status
Approach temperature differential
Free cooling percentage
Chiller lockout status during economizer operation
Valves to Isolate Pumping Loop
Isolation valve position/status (open/closed/modulating)
Pump status/command (primary/secondary)
Loop differential pressure (before/after valve)
Flow rate through isolated loop
Supply/return temperatures in isolated loop
Valve feedback vs. command
Improved Pump Differential Pressure Control
Pump differential pressure (actual)
Pump differential pressure setpoint
Pump speed % (VFD)
System flow rate
Load demand variable (determining DP reset)
Most open valve position (if available)
System pressure drop indicators
Pump motor amperage/power
Improved Outside Air Minimum Ventilation Control
Outside Air Damper position %
Outside Air CFM (calculated or measured)
Minimum OA setpoint
Supply fan VFD %
Mixed Air Temperature
Outside Air Temperature
Return Air Temperature
Building occupancy level
Ventilation effectiveness factor
CO2 levels (if integrated with DCV)
Economizer lockout status
Damper calibration verification points
Improved Cooling Tower Controls
Cooling Tower Fan #1, #2, #3 (etc.) speed %
Condenser Water Supply Temperature
Condenser Water Return Temperature
Condenser Water Temperature Setpoint
Outside Air Temperature (dry bulb)
Outside Air Humidity/Wet Bulb Temperature
Cooling tower approach temperature
Chiller condenser load %
Tower bypass valve position (if applicable)
Tower fill condition indicators (if monitored)
Water makeup flow rate

## PSE Only - Scope Review
Scope Review - Contractors schedule this w/ Commissioning@pse.com
Project Name | 0
BEFORE THE MEETING
1. Have the controls contractor fill out the Worksheet tab as much as they can
2. If possible, attain a utility data release form for the contractor, signed by the customer
3. If a data release form is provided, pull elec and/or gas bill history and enter in on the Worksheet tab
DURING THE MEETING
Describe the HVAC system being affected by this project:
Describe the GUI, it's functionality, who has access, and its age:
Discuss adds & improves, and review written explanations in Worksheet boxes:
List any significant base/process loads like refrigeration, a pool, a data center, large DHW, etc.:
What is the baseline year % occupancy? Is this anticipated to change? What is the occupancy schedule?
Has the facility experienced extended vacancies? If so, what changes were made? (e.g. schedules,
setpoints, additional cleaning shifts, outside air intake, demand control ventilation disables, etc)
When is construction expected to begin?
Is the customer interested in Demand Response? If so, forward to businessdemandresponse@pse.com

## PSE Only - DSMc Inputs
DSMc Measures |  |  |  | Scope of Work
Base |  |  |  | Background Info | Baseline Assumptions
Library Measure Name | HVAC Control - Base - Custom | Library Measure Ref# | 10049 | [State the name of the customer, the sq ft of the building, and any other brief background info on the customer. Describe the existing HVAC system(s) serving the building(s). State what sequences are being added or improved. Include any notes about building occupancy and other concurrent projects. Note the EUI compared to the EUIt to indicate opportunity for savings.] | The existing HVAC controls system is accurately defined in the HVAC Controls Worksheet.
Full or Incr? | Full | Est'd Completion Date
Proposed Assumptions
Measure Cost Electric | 0 | Electric Load Type | Misc |  | There will be a combination of added and/or improved sequences per the HVAC Controls Worksheet. |  | FAC | % of FAC | FAC Prorated MC
kWh Savings Estimated | 0 | Library Measure Life kWh | 10 | Project Specifications |  | Base Elec | 0 |  | based on base% savings
Entered Measure Life kWh | 10 | Calc Measure Life Electric | 10 | For Base Incentive: The contractor shall upgrade the HVAC controls to those described on the HVAC Controls Worksheet. All sequences applicable to the building must meet their associated 2021 WA Energy Code requirements. The contractor shall provide a Facility Guide to the building operator and PSE which includes the items on the Facility Guide tab of the HVAC Controls Worksheet. The contractor shall provide training to educate the building operator on the proper operation of the HVAC control system. For Performance Incentive: The performance incentive listed in this agreement is the maximum incentive possible. The final performance incentive will be based on the actual savings above the base incentive savings during the performance period. See the HVAC Controls Worksheet for incentive amounts at various savings increments. The minimum length of the performance period will be 12 months. The start date of the performance period will be when the base grant has been paid but may be adjusted at PSE’s discretion. PSE will determine and calculate the savings using standard engineering practices at the end of the performance period. The baseline and performance period consumption will be adjusted based on the independent variables that impact consumption, which may include weather, occupancy hours, production units, savings from other PSE funded projects, and significant changes in operations, plug, or process loads. The customer shall notify PSE of any major changes to the applicable variables. | Energy Analysis Methodology | Base Gas FAC | 0 |  | based on base% savings
Grant Amount Electric | 0 | Baseline Electric Energy Use | 0 |  | The base savings are assumed to be 3-5% of the total building use, depending on what sequences are being added and/or improved. Performance savings are calculated based on building performance.
kW Reduction | Leave Blank |  |  |  |  | Perf Elec | 0 | #DIV/0! | #DIV/0!
[6 empty] | Perf Gas | 0 | #DIV/0! | #DIV/0!
Measure Cost Therm | 0 | Gas Load Type | Space Heating |  |  | *Divides the remaining costs after 0.5*totcost - base incent
Therm Savings Estimated | 0 | Library Measure Life Therm | 10 |  | M&V Requirements | between the two fuels
Entered Measure Life Therm | 10 | Calc Measure Life Therm | 10 |  | For Base Incentive: The contractor shall provide PSE the final sequences of operation for pre-approval prior to installation. PSE will verify that the added and/or improved sequences of operation meet the 2021 WA Energy Code requirements. PSE may check additional sequences to confirm code compliance. The building operator shall demonstrate the ability to display and adjust schedules, set points, and basic control sequences like duct static reset and zone-level scheduling. The building operator must also show how to set up trend graphs and how to access the Facility Guide. The contractor-provided Facility Guide must include all items from the Facility Guide tab of the HVAC Controls Worksheet. For Performance Incentive: PSE shall review and analyze metered energy data and any facility changes provided by the customer to determine if the facility meets or exceeds the performance incentive threshold. | *Assumes we can fund up to 50% of full project cost
Grant Amount Therm | 0 | Baseline Therm Energy Use | 0
Total Measure Cost | 0 | [9 empty] | Costs from 2025 AF
[6 empty] | *Base incent is currently capped at 0.35*totCost |  |  |  | Electric Cost Effectiveness Standard (¢ per kWh) 2024/2025 | [6 empty] | Gas Conservation Cost Effectiveness Standard ($/therm) 2024/2025
Performance | [5 empty] | *Perf incent is capped at 0.5*totCost-base incent | [10 empty] | Updated: 11/03/23
Library Measure Name | HVAC Control - Performance - Custom | Library Measure Ref# | 11912 |  |  | Should perf incent be capped at 0.35*totCost-base incent? |  |  |  | Measure Life | elec htg | clg | dhw | refr | Misc | hort | Measure Life | NG space ht | dhw | process
Full or Incr? | Full | Est'd Completion Date |  |  |  | Current program caps base+perf at 0.5*totCost |  |  |  | 1 | 18.1353 | 12.1646 | 10.2324 | 13.5305 | 13.8301 | 14.1919 | 1 | 1.5499 | 1.3989 | 1.3867
[6 empty] | *Funding rate as a fraction of FAC is what causes |  |  |  | 2 | 35.1093 | 23.5551 | 19.8049 | 26.196 | 26.7735 | 27.4845 | 2 | 3.052 | 2.7641 | 2.7409
Measure Cost Electric |  | Electric Load Type | Misc |  |  | it to be difficult to estimate incents at various %. Gas has a higher incent/cost |  |  |  | 3 | 51.4519 | 34.6883 | 29.1701 | 38.4636 | 39.2962 | 40.3434 | 3 | 4.4863 | 4.071 | 4.0375
kWh Savings Estimated | 0 | Library Measure Life kWh | 10 |  |  | ratio which makes the gas perf grant cap out before elec. |  |  |  | 4 | 66.7045 | 45.0912 | 37.8683 | 49.8835 | 50.9595 | 52.3206 | 4 | 5.8283 | 5.2974 | 5.2542
Entered Measure Life kWh | 10 | Calc Measure Life Electric | 10 |  |  | Caps out at ((0.5*totCost-basecost)*FAC fraction) |  |  |  | 5 | 80.9493 | 54.7327 | 45.9091 | 60.4974 | 61.7976 | 63.4452 | 5 | 7.118 | 6.4787 | 6.4266
Grant Amount Electric | 0 | Baseline Electric Energy Use | 0 |  |  | *Can we use incent rate to split perf costs instead of FAC? |  |  |  | 6 | 94.1135 | 63.7164 | 53.3109 | 70.3598 | 71.8463 | 73.7576 | 6 | 8.3359 | 7.6024 | 7.5427
kW Reduction | Leave Blank |  |  |  |  | This would allow us to estimate incents are diff levels |  |  |  | 7 | 106.3571 | 72.02 | 60.1297 | 79.4863 | 81.1465 | 83.3049 | 7 | 9.4571 | 8.6422 | 8.5761
[10 empty] | 8 | 119.2118 | 81.1984 | 67.9003 | 89.4209 | 91.2418 | 93.635 | 8 | 10.5262 | 9.6415 | 9.5699
Measure Cost Therm |  | Gas Load Type | Space Heating |  |  |  | Incent basis |  | Prorated MC | 9 | 131.3047 | 89.8201 | 75.1981 | 98.736 | 100.714 | 103.3325 | 9 | 11.5798 | 10.6313 | 10.555
Therm Savings Estimated | 0 | Library Measure Life Therm | 10 |  |  | base elec |  |  |  | 10 | 142.597 | 97.9162 | 81.9869 | 107.45 | 109.564 | 112.3873 | 10 | 12.6263 | 11.6138 | 11.5325
Entered Measure Life Therm | 10 | Calc Measure Life Therm | 10 |  |  | base gas
Grant Amount Therm | 0 | Baseline Therm Energy Use | 0
Total Measure Cost | [5 empty] | perf elec
perf gas

## PSE Only - Bldg Changes
Performance Period Building Changes
Project Name | 0
Describe what specifically was done to get the maximum energy efficiency performance incentive:
List any addional energy efficiency projects completed during the performance period:
Describe any changes to:
Occupancy:
Tenant Type/Space Use (e.g. office, lab, classrooms):
Process loads (computer lab, refrigeration, pool, kitchen, etc):
Major Equipment (e.g. Lighting, HVAC units, boilers, chillers, etc):
Building Size or Occupied Area:
Has the facility experienced extended vacancies? If so, what changes were made? (e.g. schedules,
setpoints, additional cleaning shifts, outside air intake, demand control ventilation disables, etc)

## Lookup 1 (hidden)
N/A or Meets Code | Standard 62.1-2016 Outdoor Air Rates (Table 6.2.2.1)
Add |  | IP |  | SI |  | Default Occupant Density
Improve | Occupancy Category | Rp (cfm/per) | Ra (cfm/ft2) | Rp (L/s-per) | Ra (L/s-m2) | #/1000 ft2 (#/100 m2)
| Art classroom | 10 | 0.18 | 5 | 0.9 | 20
| Auditorium seating area | 5 | 0.06 | 2.5 | 0.3 | 150
| Bank vaults/safe deposit | 5 | 0.06 | 2.5 | 0.3 | 5
Data Center | Banks or bank lobbies | 7.5 | 0.06 | 3.8 | 0.3 | 15
Large DHW | Barbershop | 7.5 | 0.06 | 3.8 | 0.3 | 25
Refrigeration | Barracks sleeping areas | 5 | 0.06 | 2.5 | 0.3 | 20
Pool | Bars, cocktail lounges | 7.5 | 0.18 | 3.8 | 0.9 | 100
Occ Adj. (<95%) | Beauty and nail salons | 20 | 0.12 | 10 | 0.6 | 25
Other (describe) | Bedroom/living room | 5 | 0.06 | 2.5 | 0.3 | 10
| Booking/waiting | 7.5 | 0.06 | 3.8 | 0.3 | 50
| Bowling alley (seating) | 10 | 0.12 | 5 | 0.6 | 40
kWh | Break rooms (General) | 5 | 0.06 | 2.5 | 0.3 | 50
Therm | Break rooms (Office) | 5 | 0.12 | 2.5 | 0.6 | 50
| Cafeteria/fast-food dining | 7.5 | 0.18 | 3.8 | 0.9 | 100
| Cell | 5 | 0.12 | 2.5 | 0.6 | 25
Incomplete - Contact PSE when Ready | Classrooms (age 9 plus) | 10 | 0.12 | 5 | 0.6 | 35
Complete | Classrooms (ages 5–8) | 10 | 0.12 | 5 | 0.6 | 25
| Coffee stations | 5 | 0.06 | 2.5 | 0.3 | 20
Select | Coin-operated laundries | 7.5 | 0.12 | 3.8 | 0.6 | 20
No | Common corridors | 0 | 0.06 | 0 | 0.3
Yes | Computer (not printing) | 5 | 0.06 | 2.5 | 0.3 | 4
| Computer lab | 10 | 0.12 | 5 | 0.6 | 25
| Conference/meeting | 5 | 0.06 | 2.5 | 0.3 | 50
| Corridors | 0 | 0.06 | 0 | 0.3 | 0
| Courtrooms | 5 | 0.06 | 2.5 | 0.3 | 70
| Daycare (through age 4) | 10 | 0.18 | 5 | 0.9 | 25
| Daycare sickroom | 10 | 0.18 | 5 | 0.9 | 25
| Dayroom | 5 | 0.06 | 2.5 | 0.3 | 30
| Disco/dance floors | 20 | 0.06 | 10 | 0.3 | 100
| Dwelling unit | 5 | 0.06 | 2.5 | 0.3 | 2
| Freezer and refrigerated spaces (<50°F) | 10 | 0 | 5 | 0 | 0
| Gambling casinos | 7.5 | 0.18 | 3.8 | 0.9 | 120
| Game arcades | 7.5 | 0.18 | 3.8 | 0.9 | 20
| General manufacturing (excludes heavy industrial using chemicals) | 10 | 0.18 | 5 | 0.9 | 7
| Guard stations | 5 | 0.06 | 2.5 | 0.3 | 15
| Gym, sports arena (play area) | 20 | 0.18 | 10 | 0.9 | 7
| Health club/aerobics room | 20 | 0.06 | 10 | 0.3 | 40
| Health club/weight rooms | 20 | 0.06 | 10 | 0.3 | 10
| Kitchen (cooking) | 7.5 | 0.12 | 3.8 | 0.6 | 20
| Laundry rooms within dwelling units | 5 | 0.12 | 2.5 | 0.6 | 10
| Laundry rooms, central | 5 | 0.12 | 2.5 | 0.6 | 10
| Lecture classroom | 7.5 | 0.06 | 3.8 | 0.3 | 65
| Lecture hall (fixed seats) | 7.5 | 0.06 | 3.8 | 0.3 | 150
| Legislative chambers | 5 | 0.06 | 2.5 | 0.3 | 50
| Libraries | 5 | 0.12 | 2.5 | 0.6 | 10
| Lobbies | 5 | 0.06 | 2.5 | 0.3 | 150
| Lobbies/prefunction | 7.5 | 0.06 | 3.8 | 0.3 | 30
| Main entry lobbies | 5 | 0.06 | 2.5 | 0.3 | 10
| Mall common areas | 7.5 | 0.06 | 3.8 | 0.3 | 40
| Media center | 10 | 0.12 | 5 | 0.6 | 25
| Multipurpose assembly | 5 | 0.06 | 2.5 | 0.3 | 120
| Multi-use assembly | 7.5 | 0.06 | 3.8 | 0.3 | 100
| Museums (children’s) | 7.5 | 0.12 | 3.8 | 0.6 | 40
| Museums/galleries | 7.5 | 0.06 | 3.8 | 0.3 | 40
| Music/theater/dance | 10 | 0.06 | 5 | 0.3 | 35
| Occupiable storage rooms for liquids or gels | 5 | 0.12 | 2.5 | 0.6 | 2
| Occupiable storage rooms for dry materials | 5 | 0.06 | 2.5 | 0.3 | 2
| Office space | 5 | 0.06 | 2.5 | 0.3 | 5
| Pet shops (animal areas) | 7.5 | 0.18 | 3.8 | 0.9 | 10
| Pharmacy (prep. area) | 5 | 0.18 | 2.5 | 0.9 | 10
| Photo studios | 5 | 0.12 | 2.5 | 0.6 | 10
| Places of religious worship | 5 | 0.06 | 2.5 | 0.3 | 120
| Reception areas | 5 | 0.06 | 2.5 | 0.3 | 30
| Restaurant dining rooms | 7.5 | 0.18 | 3.8 | 0.9 | 70
| Sales (except as below) | 7.5 | 0.12 | 3.8 | 0.6 | 15
| Science laboratories | 10 | 0.18 | 5 | 0.9 | 25
| Shipping/receiving | 10 | 0.12 | 5 | 0.6 | 2
| Sorting, packing, light assembly | 7.5 | 0.12 | 3.8 | 0.6 | 7
| Spectator areas | 7.5 | 0.06 | 3.8 | 0.3 | 150
| Stages, studios | 10 | 0.06 | 5 | 0.3 | 70
| Supermarket | 7.5 | 0.06 | 3.8 | 0.3 | 8
| Swimming (pool & deck) | 0 | 0.48 | 0 | 2.4 | 0
| Telephone closets | 0 | 0 | 0 | 0 | 0
| Telephone/data entry | 5 | 0.06 | 2.5 | 0.3 | 60
| Transportation waiting | 7.5 | 0.06 | 3.8 | 0.3 | 100
| University/college laboratories | 10 | 0.18 | 5 | 0.9 | 25
| Warehouses | 10 | 0.06 | 5 | 0.3 | 0
| Wood/metal shop | 10 | 0.18 | 5 | 0.9 | 20

## Lookup 2 (hidden)
PSE Both |  |  | Therm | None
PSE Electric |  |  | kWh | Electric
PSE Gas |  |  |  | Gas
| Electric Cost Effectiveness Standard 2014/2015 Cents per KWH |  |  |  |  | Gas Conservation Cost Effectiveness Standard, 2014/2015
Measure | Electric Space Heating | Misc. | Summer Cooling |  | Measure | Space Heating (Retrofit) | Hot Water (DHW) | Process
Life | 1 | 3 | 4 |  | Life | 1 | 2 | 3
1 | 19.0056 | 7.0071 | 4.0881 |  | 1 | 0.51069 | 0.39888 | 0.39797
2 | 36.7559 | 13.6138 | 7.8658 |  | 2 | 1.0044 | 0.78265 | 0.78063
3 | 53.4009 | 19.8852 | 11.528 |  | 3 | 1.6142 | 1.1901 | 1.1515
4 | 69.409 | 26.1202 | 15.3676 |  | 4 | 2.2171 | 1.6103 | 1.5377
5 | 84.7398 | 32.3115 | 19.3536 |  | 5 | 2.8165 | 2.0407 | 1.9351
6 | 99.3874 | 38.4244 | 23.4189 |  | 6 | 3.4047 | 2.4763 | 2.3401
7 | 113.0664 | 44.1083 | 27.1255 |  | 7 | 3.9784 | 2.9006 | 2.7361
8 | 125.8628 | 49.5799 | 30.7824 |  | 8 | 4.5271 | 3.3093 | 3.1183
9 | 137.945 | 54.7101 | 34.2145 |  | 9 | 5.0456 | 3.6936 | 3.478
10 | 149.4308 | 59.6265 | 37.5559 |  | 10 | 5.5436 | 4.0667 | 3.8273
11 | 160.2226 | 64.2782 | 40.7459 |  | 11 | 6.0141 | 4.4165 | 4.1531
12 | 170.4588 | 68.6895 | 43.7598 |  | 12 | 6.4626 | 4.7533 | 4.4692
13 | 179.9704 | 72.8829 | 46.6274 |  | 13 | 6.8904 | 5.0757 | 4.7724
14 | 188.8698 | 76.841 | 49.3563 |  | 14 | 7.2943 | 5.3798 | 5.0586
15 | 197.3673 | 80.622 | 51.9918 |  | 15 | 7.6815 | 5.6713 | 5.3328
16 | 205.3812 | 84.2013 | 54.5101 |  | 16 | 8.0518 | 5.9514 | 5.5965
17 | 212.9048 | 87.5899 | 56.9135 |  | 17 | 8.4046 | 6.2179 | 5.848
18 | 220.0482 | 90.8184 | 59.2106 |  | 18 | 8.7442 | 6.476 | 6.0921
19 | 226.6372 | 93.8395 | 61.3547 |  | 19 | 9.0658 | 6.7211 | 6.3241
20 | 232.856 | 96.7116 | 63.411 |  | 20 | 9.3727 | 6.9544 | 6.5447
21 | 238.7029 | 99.4256 | 65.3621 |  | 21 | 9.6635 | 7.1759 | 6.7544
22 | 244.201 | 101.9905 | 67.2134 |  | 22 | 9.9389 | 7.3863 | 6.9538
23 | 249.3719 | 104.4147 | 68.9701 |  | 23 | 10.1999 | 7.5861 | 7.1434
24 | 254.2357 | 106.7063 | 70.6372 |  | 24 | 10.4472 | 7.7758 | 7.3237
25 | 258.8114 | 108.8727 | 72.2192 |  | 25 | 10.683 | 7.9564 | 7.4951
26 | 263.1168 | 110.921 | 73.7206 |  | 26 | 10.9066 | 8.1278 | 7.658
27 | 267.1683 | 112.8578 | 75.1456 |  | 27 | 11.1183 | 8.2907 | 7.813
28 | 270.9815 | 114.6894 | 76.498 |  | 28 | 11.319 | 8.4454 | 7.9603
29 | 274.571 | 116.4217 | 77.7817 |  | 29 | 11.5093 | 8.5923 | 8.1003
30 | 277.9503 | 118.0603 | 79.0002 |  | 30 | 11.6907 | 8.7321 | 8.2335
Note: These costs include the conservation credit. |  |  |  |  | Note: These costs do not include a conservation credit.

## Notes (hidden)
Worksheet Creator: Tyson Schmitt
*Lower scaling for plant and optional - too complicated
*Base scaling on deltaEUI? -too problematic
*If 30% below EUIt, performance-only or provide further details? - low savings flag
*Requirements details - need code refs? Update details?
*SCL requires: site visit, invoice, Cx report, as-built SOO, gui screenshots showing correct operation (no cust training, no trends or FPTs, no facility guide)
*SCL groups sequences by type - scheduling, ventilation control, lockouts, energy monitoring, resets, demand control, misc
*Perf cap at 50% cost for grant? Should we write perf grant for 20-25% savings?
*Add analytics as an add? FDD
*Controls optimization? Like for like - added General sequence optimization
*MF controls? For high-rise. How do we calculate? Go through MF retro audit, then eligible for incent after? Further complicates controls cals?
*Need examples
*Any other documents we can bring into this excel file?
*DR controls? C403.4.1.7
Adding function? IF not, O&M or Cx. How does one add a sequence? What is the exact process?
Installing new controllers, new GUI, controls perf based
Keeping controllers, optimizing sequences, EBCx
TAB only shows post tell contractor about increased ventilation
O&M less than Cx + HVAC controls <3
Bulk of payment on performance?
Performance 10%
Stepped incent for base, still perf
Scope review checkbox on worksheet? Need questionnaire
Less than 3 adds, custom calc w/no perf?
No base savings tied to incentive? - problem with this - what bout bldg not modeling well?
3% floor for 0 adds
Keep incent at $0.45. 3% min O&M, 4% 1 add, 5% 2 add, 6% 3 add.
o&m - document what changes made
Core adds vs supplemental adds?
Do we use other utility bill in this?
Additions
*added 0 perf savings limiter
Scope Review at top + tab
2nd Other
half points adds/improves
OA calibration box + wording on tab
Highest perf savings 25%
<1 add 25% cost cap (12.5% gas only)
Sequence details have interpretive elements, are not verbatim code. Do we remove interpretive elements?
Could just have code section by sequence
We need to explicitly state somewhere that all sequences need to be brought up to code. Maybe in SoW.
*need code refs? Update details? I found code sections for main sequences, but didn't fully update details.
Do we use other utility bill in this?
v3.5
Removed hyperlinks and sequence details
Updated some of the SoW language
v3.6
Looked up all sequence sections and added Energy Code tab
Wrote sequences for any not in the Code
Updated some sequence names
added point structure
Made 0 adds cap at 25% cost
Added link to webpage on Instructions tab
Formatted pages to print properly
hyperlinked to code
added % of EUI
v3.7
Fixed Project_Type references in calcs
Added cells to OA Calibration
v3.8
Fixed AP33 & AP34 on DSMc tab to use adjcost. Was 0.5*totCost. Did same with D43-45 on Worksheet tab. D28-30 too.
v3.9-4.0
Made <1 add projects have no base incentive, and be ineligible entirely
Updated content and formatting on FAQ and instruction pages. Added links on instruction page
Updated Facility Guide
OA Calibration references Lookup 1 table now
Added "Send to PSE" for when OA Calibration is marked as done on worksheet tab
Decided to not adjust baselines for occupancy. Will only adjust during performance period if changes occur.
PSE project cost is no longer halved again for 0 adds
11/20 - Various updates to FAQ page
Various hyperlink and formatting updates to Instructions, Facility Guide, and Worksheet pages
Added contact SME for <90% OA compared to code to Instruction tab
Added totCost*0.15 to min calc for base gas-only incent
v4.1
Formatting/minor content updates
Changed Disclaimer to Acknowledgement
Updated FAQ
v4.2-4.3
updated FAQ
added iferror formulas throughout
v4.3.1-2
renamed FAQ tab to Incentive Pathway, and updated custom capital and O&M
Added scope review check to Worksheet tab, with red text if no
Added step 1 to instructions to confirm code compliance
changes Holly's email to Cx@pse.com
updated point structure
2026 v1.0
Final formatting and locked
Light SoW updates

## DoC EUI Existing Bldg (hidden)
Department of Commerce Building Categories | Regionally Adjusted Mean EUI Existing Bldgs (kBTU/sf)
Admin/Professional Office | 63
Bank/Other Financial | 69
Clinic/Other Outpatient Health | 90
College/University | 102
Convenience w/Gas Station | 244
Courthouse | 101
Distribution/Shipping Center | 36
Dorm/Fraternity/Sorority | 88
Elementary/Middle School | 49
Enclosed Mall | 58
Entertainment/Culture | 67
Fast Food | 427
Government Office | 66
Grocery/Food Market | 191
High School | 48
Hospital/Inpatient Care | 196
Hotel | 68
Laboratory | 237
Library | 56
Medical Office (Diagnostic) | 60
Medical Office (Nondiagnostic) | 90
Motel or Inn | 74
Mulifamily (mixed use only) | 32
Nonrefrigerated Warehouse | 36
Nursing Home/Assisted Living | 78
Other Classroom Education | 49
Other Lodging | 71
Other Office | 66
Other Public Assembly | 55
Other Public Order and Safety | 66
Other Retail | 55
Other Service | 66
Police Station | 65
Post Office/Postal Center | 51
Preschool/Daycare | 59
Prison | 101
Recreation | 73
Refrigerated Warehouse | 121
Religious Worship | 39
Repair Shop | 36
Restaurant/Cafeteria/Bar | 361
Retail Store | 68
Social/Meeting | 50
Strip Shopping Mall | 55
Technology/Science Service | 66
Transporation Station | 55
Vehicle Dealership/Showroom | 59
Vehicle Service/Repair Shop | 60
Vehicle Storage/Maintenance | 41
Veterinary | 90
Wholesale Club | 68