## Instructions
The PSE Building Tune-Up program focus is to optimize the operation of existing equipment, fine tune the systems to meet the current facility requirements, and save energy.
PSE Building Tune-up Process:
1. Customer submits a pdf of the completed following documents to commissioning@pse.com:
a. "Pre-screen" tab
b. Submit "PSE Bldg Tune-up Specialist Form 7560" if not already approved by PSE or through the Seattle Tune-up process
c. PSE project application form
2. PSE Energy Management Engineer (EME) will evaluate the documentation and current utility billing information to determine eligibility.
3. Kickoff meeting with PSE and the Building Tune-Up Specialist to discuss program commitments, benefits, and performance/grant targets related to the implementation of this program
4. Once PSE approves the project, a grant is created for initial and performance phases.
5. The Building Tune-Up Specialist performs an initial review of your building’s systems to identify and report both potential capital and O&M opportunities for evaluation and implementation (Findings Checklist and M&V tabs).
6. The Building Tune-Up Specialist enters their findings in the spreadsheet to generate the report for PSE and the customer (Final Report + M&V Report tabs)
7. PSE EME will confirm the completion of the Project and prepare a payment request for the base grant amount and the performance period (10-12 months) will begin.
8. Following the performance period, PSE EME will evaluate the annual energy savings from the tune-up and submit a payment request for the appropriate performance grant amount.
Program Incentive Structure
| PSE Gas | PSE Electric | PSE Gas & Electric
Base Incentive >> | 2000 | 4000 | 5000
Performance Incentive >> | $0.80/therm | $0.05/kWh
(period of 10-12 months)
Tune-up Report’s Purposes:
• Document and summarize what was accomplished
• Outline initial issues and potential improvements found
• List any fixes on and off the required list of measures
• Provide a good understanding of the energy use in the building
• Demonstrate the benefits of the process to the owner’s management
• Assist in the prioritization of future capital projects
Tune-up Report Content Requirements:
1. Executive Summary of Building Tune-up (1 pages)
a. General system descriptions and condition (HVAC, lighting and other major energy use equipment)
2. PSE Form (Pre-screen) which includes the following information.
a. Building name
b. Building square footage
c. Building uses – hours of operation, approximate square footages & systems specific for each use
d. Annual energy use (billing, EIS, EUI)
e. Past and future changes to systems and building use
f. Basic eligibility for program
3. List of quick fixes with estimated energy savings and pre and post conditions documentation.
a. Issues found that are low-cost/no-cost
4. Current Facility Requirements Summary
a. Schedules (equipment & occupants)
b. Ventilation
c. Sensor Calibration

## Pre-screen
Facility: | [6 empty] | Application Date:
Owner:
Senior Operations: | [6 empty] | Management:
Building Details
| Total Area: |  | 50000 | Space type: |  | Office |  | Annual Usage: | 1000000 |  | kWh
[9 empty] | 20000 |  | therms
| Occupied |  | Start (AM) |  | End (PM)
| Weekday: |  | 6 |  | 5
Weekend:
Other:
This document serves as an initial screening tool to determine whether your building(s) would be a good candidate for this program or other programs within the PSE efficiency portfolio. Please mark the statements below that apply and submit to your PSE representative with an application for consideration.
PSE Application
Minimum Qualifications: |  |  |  | TRUE |  | TRUE
| Building(s) use |  |  | PSE Gas |  | PSE Electric
PSE gas only customers must use gas for space heating (e.g.: uses a condensing boiler, ventilation or make-up air heated by gas, not just for tempering the supply air)
Building(s) collectively have ≥ 50,000 conditioned square footage OR use significantly more energy than a typical office building (e.g.: 24/7 facility, museum, medical facility, MOB).
No major upgrades anticipated that will change how the equipment is operated (e.g. replacing constant volume HVAC with VAV, replacing controls).
No plans for controls system replacement or major upgrades within the next 5 years.
Building is at least 75% occupied
Additional Considerations to Qualify:
Building(s) is ≥ 1.5 year old.
Building energy use is > average for typical building of this type. Be sure to consider whether high use is controllable (associated with HVAC) or not (may include server rooms, DHW, Laundry, or other process loads).
Building Energy Use Index:
| Current: |  |  | 108.24 | Total kBTU/sq.ft. |  | 20 | kWh/sq.ft. | 0.4 | Therms/sq.ft
| Avg. for similar buildings: |  |  | 56.8978 | Total kBTU/sq.ft. |  | 11.8439 | kWh/sq.ft. | 0.16486 | Therms/sq.ft
Building has had several changes in use, or several different tenants since it was constructed.
Building does NOT have some of the energy efficient control sequences listed below (mark missing features):
Duct static/discharge air temperature/HW/CW/CHW reset based on load
Staging of chiller or boilers based on unit efficiency
Deadband for room temp setpoints
Optimum start/stop
VFDs
Other?
Building has never been commissioned by a third party (new or existing).
[5 empty] | If it has, date of last commissioning (Cx): |  |  | Cx Agent:
Ventilation rate has never been checked and there are no indoor air problems.
Building has had a lot of comfort, other issues, and/or does not seem to work right.
HVAC/lighting controls are not regularly tested, only basic maintenance has been done (e.g. change filters/belts).
Main HVAC system is NOT single zone packaged RTUs with wall stats.
HVAC systems have a BAS or DDC system. Last upgrade:
HVAC systems are complex systems:
Central hot water (boiler plant)
Central chilled water (chiller plant)
Variable Air Volume (VAV)
Multi-zone RTU
Other?
Major Reasons to Proceed:
List other reasons this is a good candidate. Include HVAC/lighting/controls issues building has had, findings from walk-through:
Give basic description of facility: # of buildings/systems in project, general hours of operation, HVAC type, lighting controls type, use of building, are there a lot of computers used, % of space for server rooms.
List changes in use or equipment in the past year and expected for the next 5 years. Explain briefly how one would easily adjust for this change in a billing savings analysis:
Other PSE Program that would help customer save energy:
Other Comments/Notes:

## IncentiveEst (Optional)
Building Tune-up Incentive/Goals: Calculator - Ver 9/14/21 | [6 empty] | 2021-09-14 09:41
Project Name: | PSE Customer, Building Name - Tune-up
Customer: | PSE Customer
Address: | 1234
Renton, WA 98057
Project Type | PSE gas/other elec | Date: | 2020-03-26
| Sch 24 | Gas Rate: | Sch 31
Provider Cost: | 15000
Implementation Cost: | 5000 | $0.1/sq.ft.
SF: | 50000
Utility Data and Investment Variables | [8 empty] | Years | Invested | Incentive | Energy Savings | Net Annual (MIN) | PV Rate (MIN) | PV Rate (MIN) | Initial investment | IRR Calc MIN
Annual Therms: | 20000 | 0.4 | th./sq.ft. /yr. | [5 empty] | Yr 0 | -20000 | 1000 | 5.0341 |  |  |  | 20000 | -18822.4
Annual kWhs: | 1000000 | 20 | kWh/sq.ft./yr. | [5 empty] | Yr 1 |  | 177.6 | 5034.0676 | 5039.1017 | 4581.0015 |  | Incentive | 5039.1017
Total Building Energy Use |  | 108.24 | kBTU/sq.ft./yr. | [5 empty] | Yr 2 |  |  | 4792.4324 | 4792.4324 | 3960.6879 |  | 1177.6 | 4792.4324
Prefered Discount Rate: |  | 10% | (NPV Calc.) | [5 empty] | Yr 3 |  |  | 4562.3956 | 4562.3956 | 3427.7953 |  |  | 4562.3956
Graph of Cash Flow MAX/MIN Est.): |  | MAX | [6 empty] | Yr 4 |  |  | 4343.4006 | 4343.4006 | 2966.6011 |  |  | 4343.4006
[9 empty] | Yr 5 |  |  | 4134.9174 | 4134.9174 | 2567.4584 |  |  | 4134.9174 | Project Cash Flow (MAX Estimate)
Incentive Estimates | [17 empty] | Years | Invested | Incentive | Energy Savings | SPB | x | y
| Tune-up | Performance | [12 empty] | 17503.5442 |  |  | Yr 0 | -20000 | 1000 | 5.0341 |  | 2.9213 | 0
Minimum tune-up Incentive | [8 empty] | Years | Invested | Incentive | Energy Savings | Net Annual (MAX) | PV Rate (MAX) | PV Rate (MAX) | IRR Calc MAX |  | Yr 1 | 0 | 97.6 | 9755.8116 |  | 2.9213 | 1
Incentives | 1000 | [7 empty] | Yr 1 | 0 | 97.6 | 9755.8116 | 9760.8457 | 8873.4961 |  | -18822.4 |  | Yr 2 | 0 | 0 | 9287.5327
Min. Performance Target |  | Savings | Final Cost | [5 empty] | Yr 2 | 0 |  | 9287.5327 | 9287.5327 | 7675.6468 |  | 9760.8457 |  | Yr 3 | 0 | 0 | 8841.7311
Incentives | 1000 | 177.6 | 18822.4 | [5 empty] | Yr 3 | 0 |  | 8841.7311 | 8841.7311 | 6642.9234 |  | 9287.5327 |  | Yr 4 | 0 | 0 | 8417.328
Max Performance Target |  | Savings | Final Cost | INSTRUCTIONS: Enter customer/utility data, fill all yellow cells and the existing energy use must be reduced for large uncontrollable process loads by completing the Process Loads section below. |  |  |  |  | Yr 4 | 0 |  | 8417.328 | 8417.328 | 5749.1483 |  | 8841.7311 |  | Yr 5 | 0 | 0 | 8013.2963
Incentives | 1000 | 97.6 | 18902.4 | [5 empty] | Yr 5 | 0 |  | 8013.2963 | 8013.2963 | 4975.6265 |  | 8417.328
Calculate Major Process Loads (Loads > 1%) | [14 empty] | 33916.8412
Process Load Type |  | Load kW or therm/hr. | Annual Hours | Annual Use | UOM | Description
Data Center |  |  |  | 0 | [6 empty] | All PSE (all elec)
Large DHW |  |  |  | 0 | [6 empty] | PSE elec/other gas
Refrigeration |  |  |  | 0 | [6 empty] | PSE gas/other elec
Other (describe) |  |  |  | 0
Performance Incentive Estimate Calculation
| Percent Savings | Therms | kWhs | kbtus | Base Incentive | Performance Incentive | Total Incentive | Percent Incentive
Savings MIN Target | 1.11% | 222 | 50000 | 22200 | 1000 | 177.6 | 1177.6 | 5.888%
Savings MAX Target | 0.61% | 122 | 100000 | 12200 | 1000 | 97.6 | 1097.6 | 5.488%
Baseline Energy Use |  |  | Economic Analysis
| Total Use (Actual) |  |  | Annual Cost Savings | Simple Payback (SPB) | Internal Rate of Return (IRR) | Accounting Rate of Return (ARR) | Net Present Value (NPV)*
Electric | 1000000 |  | Min. Estimate | 5029.0386 | 3.7074 | 7.121% | 22.87% | -1318.8558
Gas | 20000 |  | Max. Estimate | 9746.0656 | 1.9213 | 33.73% | 44.32% | 15094.4412
*Uses a discount rate of 7.8% for the energy savings and a 3% inflation in energy cost throughout the 5 year measure life beginning in year 2 (net 4.8% decrease).
Project Notes:
Performance Calc. | PSE Internal Use Only - Allocation by Measure
Measure Description |  |  | Measure Cost | PSE Grant | Savings | Load Type | TRC | Baseline Use
Building Tune-up Base (elec) |  |  | 0 | 0 | 0 |  | 0 | 0
Building Tune-up Performance (elec) |  |  | 0 | 0 | 0 |  | 0 | 0
Building Tune-up Base (gas) |  |  | 1000 | 1000 | 0 | Heating | -9.99 | 20000
Building Tune-up Performance (gas) |  |  | 19000 | 0 | 122 | Heating | -9.99 | 20000
Totals |  |  | 20000 | 1000
\\Sestdpt1.puget.com\Sopscci\4-Energy Efficiency\BEM\_Grants\250- CI Retro\_Commissioning\02_Building Tune-up\00_Requirements\[Building Tune-Up_Form 9-14_2021.xlsx]IncentiveEst (Optional)
Data Center
Large DHW
Refrigeration
Pool
Other (describe)
Initial Grant
Final True-up*
0
0
Note on B21: Jason Hyatt: If this is a campus project, overwrite the formula with calculated value (PSE Calculated).
Note on H40: Jason Hyatt: AVE net cash inflow / Initial investment

## Hidden (hidden)
List for Program Grant Amounts | [9 empty] | Sch_Elec (10-01-17) | Rates_Elec (¢ / kWh) | Demand ($ / kW) |  |  |  | 2019 CBSA Data - Typical PSE Comparison
Customer Type | Implementation $/sf | CX provider $/sf | Assessment |  |  | MIN |  |  | Initial Grant Calc. | Sch 25 (<20,000 kWh/mo) | 9.4196 | 7.52 | PSE | sched. | $ | PSE Electric EUI (kWh/SF) |  |  |  | PSE Gas EUI (therms)
All PSE (gas/elec) | 0.15 | 0.35 | 5000 |  |  | MAX |  |  | Performance Calc. | Sch 25 (>20,000 kWh/mo) | 7.2469 | 7.52 | SCL/PSE | SCL Rates |  | Type | Median | Q1 | Q3 | Type | Median | Q1 | Q3
All PSE (all elec) | 0.15 | 0.35 | 5000 | [6 empty] | Sch 26 - Primary | 5.6941 | 10.935 | SCL | Small GS | 0.0973 | Assembly | 7.9287 | 2.4 | 16 | Assembly | 0.44444 | 0.19 | 0.43
PSE elec/other gas | 0.1 | 0.25 | 4000 | [6 empty] | Sch 26 - Secondary | 5.8898 | 11.285 |  | Medium GS | 0.077513 | Grocery | 40.2307 | 41 | 73 | Grocery | 0.57326 | 0.42 | 0.61
PSE gas/other elec | 0.1 | 0.15 | 2000 | [6 empty] | Sch 31 | 5.6633 | 10.94 |  | Large GS | 0.089286 | Lodging | 10.8867 | 11 | 14 | Lodging | 0.43015 | 0.27 | 0.48
[10 empty] | Sch 40-HV | 5.4413 | 4.02 |  | High Demand GS | 0.0809 | Office | 11.8439 | 7.8 | 18 | Office | 0.16486 | 0.13 | 0.34
| elec savings | gas savings | [7 empty] | Sch 40-Primary | 5.5191 | 4.11 |  | PSE Rates |  | Other | 6.3892 | 4.8 | 22 | Other | 0.36156 | 0.42 | 0.83
All PSE (gas/elec) | 7% | 7% | Therm | None | [5 empty] | Sch 40-Secondary | 5.6638 | 4.2 |  | Sch 25 (<20,000 kWh/mo) | 0.094196 | Residential Care | 14.7362 | 11 | 24 | Residential Care | 0.41015 | 0.23 | 0.4
All PSE (all elec) | 7% | 0% | kWh | Electric | [5 empty] | Sch 43 | 6.5084 | 4.98 |  | Sch 25 (>20,000 kWh/mo) | 0.072469 | Food Service | 39.613 | 20 | 39 | Food Service | 2.4757 | 0.86 | 1.7
PSE elec/other gas | 7% | 0% | [7 empty] | Sch 46 | 6.0828 | 2.09 |  | Sch 26 - Primary | 0.056941 | Retail | 9.5914 | 4 | 14 | Retail | 0.29059 | 0.2 | 0.33
PSE gas/other elec | 0% | 10% |  | Gas | [5 empty] | Sch 49 | 6.1964 | 3.7 |  | Sch 26 - Secondary | 0.058898 | School | 7.392 | 6.7 | 10 | School | 0.22459 | 0.37 | 0.51
[10 empty] | Sch_NG (10-01-17) | Rates_NG ($ / therm) |  |  | Sch 31 | 0.056633 | Warehouse | 3.716 | 1.2 | 3.6 | Warehouse | 0.14154 | 0.054 | 0.21
[10 empty] | Sch 31 | 0.8186 |  |  | Sch 40-HV | 0.054413
| Electric Cost Effectiveness Standard 2014/2015 Cents per KWH |  |  |  |  | Gas Conservation Cost Effectiveness Standard, 2014/2015 |  |  |  | Sch 41 < 5,000 | 0.50559 |  |  | Sch 40-Primary | 0.055191 | *Q1 and Q3 Columns awaiting update
Measure | Electric Space Heating | Misc. | Summer Cooling |  | Measure | Space Heating (Retrofit) | Hot Water (DHW) | Process |  | Sch 41 > 5,000 | 0.47308 |  |  | Sch 40-Secondary | 0.056638
Life | 1 | 3 | 4 |  | Life | 1 | 2 |  |  | Sch 85 Interruptible <25k | 0.47736 |  |  | Sch 43 | 0.065084
5 | 56.0656 | 39.3879 | 31.9985 |  | 5 | 4.7147 | 4.0836 | 3.8424 |  | Sch 85 Interruptible 25-50k | 0.41962 |  |  | Sch 46 | 0.060828
[10 empty] | Sch 85 Interruptible >50k | 0.41682 |  |  | Sch 49 | 0.061964
Note: These costs include the conservation credit. |  |  |  |  | Note: These costs do not include a conservation credit. |  |  |  |  | Sch 86 Interruptible <1,000 | 0.62121
[10 empty] | Sch 86 Interruptible >1,000 | 0.55139
[10 empty] | Sch 87 Interruptible <25k | 0.52439
Sch 8 | 8.9485 |  | Sch_NG (11-01-13) | Rates_NG ($ / therm) | [5 empty] | Sch 87 Interruptible 25-50k | 0.46048
Sch 11 (<20,000 kWh/mo) | 8.6618 |  | Sch 31 | 0.96898 | [5 empty] | Sch 87 Interruptible 50-100k | 0.425
Sch 11 (>20,000 kWh/mo) | 6.4847 |  | Sch 41 < 5,000 | 0.67526 | [5 empty] | Sch 87 Interruptible 100-200k | 0.40271
Sch 12 - Primary | 5.0994 |  | Sch 41 > 5,000 | 0.64573 | [5 empty] | Sch 87 Interruptible 200-500k | 0.39154
Sch 12 - Secondary | 5.2951 |  | Sch 85 Interruptible <25k | 0.66765 | [5 empty] | Sch 87 Interruptible >500k | 0.38496
Sch 24 | 9.6279 |  | Sch 85 Interruptible 25-50k | 0.61191
Sch 25 (<20,000 kWh/mo) | 9.3412 |  | Sch 85 Interruptible >50k | 0.60889
Sch 25 (>20,000 kWh/mo) | 7.1641 |  | Sch 86 Interruptible <1,000 | 0.78773
Sch 26 - Primary | 5.7788 |  | Sch 86 Interruptible >1,000 | 0.72431 | [5 empty] | SCL Rates
Sch 26 - Secondary | 5.9745 |  | Sch 87 Interruptible <25k | 0.70844 | [5 empty] | Small GS | 0.0973
Sch 29 (<20,000 kWh/mo) | 7.6959 |  | Sch 87 Interruptible 25-50k | 0.64679 | [5 empty] | Medium GS | 0.077513
Sch 29 (>20,000 kWh/mo) | 6.1523 |  | Sch 87 Interruptible 50-100k | 0.61254 | [5 empty] | Large GS | 0.089286
Sch 31 | 5.7888 |  | Sch 87 Interruptible 100-200k | 0.59105 | [5 empty] | High Demand GS | 0.0809
Sch 40-HV | 5.4413 |  | Sch 87 Interruptible 200-500k | 0.58027
Sch 40-Primary | 5.5191 |  | Sch 87 Interruptible >500k | 0.57393
Sch 40-Secondary | 5.6638 | [8 empty] | Implementation Cost
Sch 43 | 6.508 | [8 empty] | 0.05
Sch 46 | 6.0489 | [8 empty] | 0.1
Sch 49 | 6.1026 | [8 empty] | 0.15
Y
N

## Findings Checklist
TOP FOUR AREAS (according to BETTER BRICKS)
Saving energy through better building operation starts with finding low-no cost opportunities with the potential for the greatest benefits. Most O&M-related energy waste falls into these major categories:
• Equipment Scheduling – Equipment runs when it is not needed.
• Sensor Error – Erroneous sensor data causes increased heating, cooling, or equipment operation, which can affect occupant comfort as well as energy consumption.
• Simultaneous Heating and Cooling – The same air gets heated and cooled, or hot and cold air streams get mixed together to make warm air.
• Outside Air Usage – Economizer (cooling with outside air; “free” cooling) does not function optimally, or excessive outside air causes increased heating and/or mechanical cooling, and sometimes too little outside air compromises indoor air quality.
*Sample size for functional testing = a minimum of 10 pieces of equipment or 10% of the population size.
Instructions for Building Tune-up Specialist - Review the checklist below and select an appropriate Status (see below). Provide a brief note of the existing field conditions. The information entered here will automatically transfer to the "Tables" tab.
"Exists" | measures can be implemented immediately and are required for tune-up
"Modify" | measures for a short-term implementation plan, anticipated low/no-cost
"Add" | measures for a long-term implementation plan, anticipated capital cost
Any measure considered "N/A" should be listed as "Add" along with an explanation for being not applicable.
Code | Assessment Element | Status | Original Field Conditions
1 | Equipment Scheduling (HVAC, lighting or other) |  |  | FALSE
1.01 | Review and match equipment schedules (including daily, weekly, seasonal, day/night, occ./unocc. hours) to occupancy hours. [EXPECTED: Schedules match operations and actual building occupancy patterns and are not manually manipulated for morning warmup/cool down.] |  |  | FALSE
1.02 | Check for equipment in override/hand mode, no controls for turning off, on/enabled regardless of need. [EXPECTED: All functional overrides within front end DDC and at point-of-use are disabled or in automatic mode.] |  |  | FALSE
1.03 | Review occupancy sensors for proper sensing, positioning, and delay period prior to power down. [EXPECTED: All lighting wired for occupancy detection powers off after ______ minutes of being unoccupied and does not shutoff when space is occupied.] |  |  | FALSE
1.04 | Review exterior lighting schedules, light or motion sensors, ensuring that lighting only illuminates with traffic and/or current sunrise/sunset times. [EXPECTED: The exterior, controlled lighting is only illuminated when traffic is expected or sensed during periods before sunrise or after sunset.] |  |  | FALSE
1.05 | Review all spaces that incorporate Demand Controlled Ventilation (DCV) and verify calibration of CO2 sensors [EXPECTED: All CO2 sensors read ambient ppm when building is unoccupied. ] |  |  | FALSE
_ | Spacer |  |  | FALSE
2 | Economizer/Ventilations Loads |  |  | FALSE
2.01 | Review the building's ventilation rates used during full heating/cooling (not economizing). [EXPECTED: All HVAC units bring in the appropriate amount of ventilation during full-heating/cooling as required by ASHRAE 62.1 standards for appropriate space types] |  |  | FALSE
2.02 | Verify proper calibration and positioning of MAT/OSAT/RAT sensors. [EXPECTED: All temperature sensors are calibrated and positioned in such a way that they report an accurate representation of the expected values and are not affected by other influences (i.e. placed in sun of contacting hot or cold surfaces). ] |  |  | FALSE
2.03 | Verify proper calibration and position of the DSP sensor. [EXPECTED: Sensor is calibrated and is located at a point in the supply duct to provide a good representation of pressure in all duct work branches.] |  |  | FALSE
2.04 | Verify the VFD displayed frequency matches with what the GUI displays. [EXPECTED: The two outputs match and verify the modulation of the motor speed.] |  |  | FALSE
2.05 | Verify that VAV box dampers modulate as expected MIN/MAX. [EXPECTED: Box dampers open and close as expected.] |  |  | FALSE
2.06 | Review economizer usage to maximize free cooling through the use of a dry bulb (changeover) temperature alone. [EXPECTED: All AHUs use a changeover temperature of ___°F (min ventilation with mechanical cooling activatates) that matches the RAT or the balance point of the building.] |  |  | FALSE
2.07 | Review integrated economizer to maximize free cooling by increasing the economizing temperature to match the RAT and allowing mechanical cooling to supplement cooling during the economizing cycle. [EXPECTED: All ventilation unit maximize economizing by matching changeover point to RAT and use an integrated economizer sequencing.] |  |  | FALSE
_ | Spacer |  | existing | FALSE
3 | Building Pressurization |  |  | FALSE
3.01 | Check for any indications of significant balancing issues (e.g. wind-tunnel effect, ajar or hard to open doors) [EXPECTED: Building pressure slightly positive to eliminate infiltration.] |  |  | FALSE
3.02 | Verify appropriate position and calibration of building pressure sensors. [EXPECTED: Sensors are appropriately calibrated and positioned in representative zone(s) for the building and/or pressure controlled zone(s). ] |  |  | FALSE
_ | Spacer
4 | Controls Problems (HVAC or lighting or other) |  |  | FALSE
4.01 | Review BAS for instances of simultaneous heating & cooling [EXPECTED: HVAC controls set to reduce or eliminate any unintended or inappropriate simultaneous heating and cooling.] |  |  | FALSE
4.02 | Review zone deadbands, SAT setpoint(s) and reset schedule for excessive reheat [EXPECTED: The supply air temperature is only cooled to meet the minimum cooling load requirements.] |  |  | FALSE
4.03 | Review BAS trending logs for instances of controls hunting, loop tuning opportunities, and/or appropriate dead bands [EXPECTED: There is no evidence of setpoints cycling repeatedly to maintain HVAC setpoints.] |  |  | FALSE
4.04 | Review mapping of control points in the control logic and on graphical user interface (sample of 10% or 20 boxes) [EXPECTED: Each point on the DDC GUI represents the correct equipment/state (end-to-end verification).] |  |  | FALSE
4.05 | Review functionality of daylighting controls where applicable [EXPECTED: Daylighting controls set or adjusted as appropriate to match actual building illumination patterns] |  |  | FALSE
4.06 | Review assignment of spaces to each zone, including appropriate schedules and loads [EXPECTED: Zone boxes grouped by tenant (or______________________) for scheduling and override.] |  |  | FALSE
_ | Spacer
5 | Controls - Setpoints |  |  | FALSE
5.01 | Review heating & cooling setpoints in each zone against the building's standard setpoints or temp. range. [EXPECTED: Zone temperature setpoints for heating and cooling are within building owner requirements at ___°F and ___°F.] |  |  | FALSE
5.02 | Review unoccupied and night setback zone temperatures [EXPECTED: Night/Unoccupied zone temps meet owner requirements: cooling ___°F or higher; heating ___°F or lower.] |  |  | FALSE
5.03 | Review duct static pressure (DSP) setpoint(s) to confirm proper reset range. [EXPECTED: DSP setpoint range is 0.5-1.5”, or better (lower). If higher explain what is keeping it at that pressure and not allowing it to go lower. ] |  |  | FALSE
5.04 | Review deadband between heating & cooling setpoints [EXPECTED: Deadband of at least a 5 °F between occupied setpoints and restricts overlap between multiple thermostats in a space.] |  |  | FALSE
5.05 | Review boiler & chiller lockout temps based on OAT [EXPECTED: Boiler plant and cooling lockout on OAT to prevent simultaneous heating and cooling and the temperatures are ___°F and ___°F. ] |  |  | FALSE
5.06 | Review supply air temperature reset schedule in control sequence and/or in BAS settings [EXPECTED: SA temperature range is 65-55 °F, or better, with at least 25% delta between SAT and room temperature.] |  |  | FALSE
5.07 | Review VAV box max & min airflow settings [EXPECTED: Box air flow is within the range specified for each box.] |  |  | FALSE
5.08 | Review chilled water temperature setpoint [EXPECTED: Chilled water setpoint optimized for efficiency as appropriate for building use and occupant needs.] |  |  | FALSE
5.09 | Review heating hot water temperature setpoint [EXPECTED: Hot water setpoint optimized for efficiency as appropriate for building use and occupant needs.] |  |  | FALSE
5.1 | Review Optimum Start settings for optimization [EXPECTED: Schedule matches occupancy and allows no more than 4 hours for warmup/cooldown.] |  |  | FALSE
5.11 | Review Optimum Stop settings and functionality [EXPECTED: Room temperature heating setpoints gradually adjust down to ___°F and cooling setpoints up to ___°F, 1-2 hours before the scheduled stop. ] |  |  | FALSE
_ | Spacer
6 | Controls - Sequence optimization |  |  | FALSE
6.01 | Compare actual VFD operation with what is required by the sequence of operation commanding modulation. [EXPECTED: VFD should modulate as demand increases and decreases.] |  |  | FALSE
6.02 | Review SAT reset setpoint schedules and reset control variable [EXPECTED: SAT reset is based on a specific temperature range: 65-55°F or better, uses slow reacting trim-and-response sequences, different interval and different controlling variables controlling this and DSP reset. ] |  |  | FALSE
6.03 | DSP reset based on load [EXPECTED: DSP reset is based on load. Low all heating, high all in cooling with reasonable diversity range 0.4-1.5” WC expected, if higher fully document reason. ] |  |  | FALSE
6.04 | HWT reset based on load not OAT. [EXPECTED: Based on load and the lowest HWT reset range is in the condensing range (below 140°F) if a condensing boiler.] |  |  | FALSE
6.05 | CHWT reset based on load not OAT. [EXPECTED: CHWT reset of at least 5°F based on zone cooling signals/valves not OSAT and is based on at least two zones excluding cooling only zones or zones with constant load, like equipment rooms. For excluded zones set air/water to meet load at the full reset temp ] |  |  | FALSE
6.06 | Condenser water temperature (CWT) reset based on load [EXPECTED: Condenser water temperature (CWT) is reset down to at least 70°F. ] |  |  | FALSE
6.07 | Review packaged cooling and/or heating staging in the control sequence [EXPECTED: All heating and cooling capacity should be gradually enabled according to load within the building and the most efficient operation.] |  |  | FALSE
6.08 | Review chiller staging [EXPECTED: Chillers are stage to use the minimal chiller plant energy (i.e. plant kW/ton for cooling tower fans, pumping, chillers) ] |  |  | FALSE
6.09 | Review boiler staging [EXPECTED: Standard boilers are staged in such a way as to minimize losses from less efficent or oversized boilers; Condensing boilers – low fire first stage and then in parallel from low to high fire.] |  |  | FALSE
6.1 | Review Optimum Start Warm-up capabilities [EXPECTED: Optimum start is allowed on for a maximum of 4 hours prior to occupancy. OA closed for warm-up and uses gas pre-heat (if available) with lock out of electric re-heat or other strip heat.] |  |  | FALSE
6.11 | Review Optimum Start Cool-down capabilities [EXPECTED: Cool-down use OA with mechanical cooling locked out (ventilation purge 1 hour before pre-cooling) and only boxes not meeting room temperature setpoint are on with primary dampers open.] |  |  | FALSE
6.12 | Review Optimum Stop (Coast) capabilities [EXPECTED: Room temperature heating setpoints are gradually adjusted down and room temperature cooling setpoints up, 1-2 hours before the scheduled stop.] |  |  | FALSE
6.13 | Review outside air tempering strategy [EXPECTED: OSA is tempered with auxiliary heat only when the OSAT reaches ___°F or if the MAT drops below setpoint.] |  |  | FALSE
6.14 | Review Demand Controlled Ventilation strategy [EXPECTED: Setpoints shall be by space type per ASHRAE Guideline 36.] |  |  | FALSE
_ | Spacer
7 | Equipment Efficiency / Load Reduction |  |  | FALSE
7.01 | Review all constant speed fan operation for variability potential [EXPECTED: All fans require the maximum CFM supplied by fans and have no variability potential or they are < 7.5 hp.] |  |  | FALSE
7.02 | Review constant speed pump operation for variable load potential where a VFD could be added or impeller trimming could be implemented [EXPECTED: There are no valves throttled down to manually slow water flow, all loads need constant flow of water, or are < 7.5 hp.] |  |  | FALSE
7.03 | Review non-Condensing HW Boiler equipment for potential replacement with condensing technology. [EXPECTED: Equipment is in good repair well inside expected life and has little potential for reducing temperatures below 140°F.] |  |  | FALSE
7.04 | Review DHW equipment for potential replacement with condensing technology. [EXPECTED: Equipment is in good repair well inside expected life.] |  |  | FALSE
7.05 | Review lighting levels in all spaces for de-lamping opportunities [EXPECTED: Lighting levels appropriate for the space use and occupant needs, dimming or de-lamping where appropriate.] |  |  | FALSE
7.06 | Review interior or exterior lighting technology for upgrade opportunities to LED or other appropriate technology [EXPECTED: All lighting fixtures have recently been replaced.] |  |  | FALSE
7.07 | Identify all interior and exterior lighting fixtures that could be controlled with occupancy, photocells, or schedule that are currently without [EXPECTED: All fixtures are controlled to minimize burn hours.] |  |  | FALSE
7.08 | Identify any single zone HVAC systems that could be candidates for DCV control (e.g. conference rooms, gyms, library,etc.). [EXPECTED: All AHUs serve multiple zones without a significant oportunity or a diverse occupancy. ] |  |  | FALSE
7.09 | Review all packaged equipment for future replacement oportunities and develop a replacement schedule. [EXPECTED: All equipment is relatively new and/or in good repair.] |  |  | FALSE
_ | Spacer
8 | Maintenance |  |  | FALSE
8.01 | Check heat exchange surfaces (coils, heat exchangers, fins) [EXPECTED: HVAC equipment cleanliness meets ANSI/ASHRAE/ACCA Standard 180‐2012 Table 5‐2, 5‐15] |  |  | FALSE
8.02 | Review filters & ductwork for any flow obstructions [EXPECTED: No obstructions to flow and clean filters] |  |  | FALSE
8.03 | Check dampers, valves, sensors, and actuators functionality [EXPECTED: Equipment functions per ANSI/ASHRAE/ACCA Standard 180‐2012 Table 5‐9, 5‐12] |  |  | FALSE
8.04 | Check steam trap for functionality and leaks [EXPECTED: Steam trap functions to standards (ANSI/ASHRAE/ACCA Standard 180‐2012 Table 5‐2, 5‐22).] |  |  | FALSE
8.05 | Review all ducting for gaps or other leakage [EXPECTED: Duct leakage minimized to meet standards (ANSI/ASHRAE/ACCA Standard 180‐2012 Table 5‐2, 5‐22).] |  |  | FALSE
8.06 | Check all dampers for leaks when they should be 100% closed [EXPECTED: Damper leakage meets ANSI/ASHRAE/ACCA Standard 180‐2012 Table 5‐9, 5‐12.] |  |  | FALSE
8.07 | Check all valves for leakage [EXPECTED: Valve leakage meets ANSI/ASHRAE/ACCA Standard 180‐2012 Table 5‐9, 5‐12 if not opening and closing fully.] |  |  | FALSE
8.08 | Review all dampers and actuators located within air handlers and verify that there are no obstructions or failures to prevent modulation. [EXPECTED: All dampers modulates as expected with no visible signs of wear or tampering.] |  |  | FALSE
8.09 | Review and identify any nuisance or missing alarms, discuss with building staff [EXPECTED: All alarms have been addressed and reviewed for potential additions without any sugestions.] |  |  | FALSE

## Tables
0 | "Exists" Measures Table: The list below consists of the energy efficiency measures which "Exist" and should be a part of the ongoing maintenance plan. Use the dropdowns on the right to estimate the savings impact. Use the notes cell to provide additional background. | [5 empty] | 0 | "Modify" Measures Table: The list below consists of recommended measures to "Modify" for improved energy efficiency at little or no cost. Use the dropdowns on the right to estimate the savings impact and potential implementation timeline. Use the notes cell to provide additional background. | [6 empty] | 0 | "Add" Measures Table: The list below consists of recommended measures to "Add" for improved energy efficiency (anticipated capital cost). Use the dropdowns on the right to estimate the savings impact and potential implementation timeline. Use the notes cell to provide additional background.
11 | [6 empty] | 11 | [7 empty] | 11
| Assessment Element | Expected Operation | Original Field Conditions | Verification Requirements | Complete? | Savings Potential |  | Assessment Element | Expected Operation | Original Field Conditions | Expected Verification | Complete? | Savings Potential | Timeline |  | Assessment Element | Expected Operation | Original Field Conditions | Expected Verification | Complete? | Savings Potential | Timeline
Notes | Explanation REQUIRED for 'N/A' measures | [5 empty] | Notes | Explanation REQUIRED for 'N/A' measures | [6 empty] | Notes | Explanation REQUIRED for 'N/A' measures
Notes | [6 empty] | Notes | [7 empty] | Notes
Notes | Explanation REQUIRED for 'N/A' measures | [5 empty] | Notes | Explanation REQUIRED for 'N/A' measures | [6 empty] | Notes | Explanation REQUIRED for 'N/A' measures
Notes | [6 empty] | Notes | [7 empty] | Notes
Notes | Explanation REQUIRED for 'N/A' measures | [5 empty] | Notes | Explanation REQUIRED for 'N/A' measures | [6 empty] | Notes | Explanation REQUIRED for 'N/A' measures
Notes | [6 empty] | Notes | [7 empty] | Notes
Notes | Explanation REQUIRED for 'N/A' measures | [5 empty] | Notes | Explanation REQUIRED for 'N/A' measures | [6 empty] | Notes | Explanation REQUIRED for 'N/A' measures
Notes | [6 empty] | Notes | [7 empty] | Notes
Notes | Explanation REQUIRED for 'N/A' measures | [5 empty] | Notes | Explanation REQUIRED for 'N/A' measures | [6 empty] | Notes | Explanation REQUIRED for 'N/A' measures
Notes | [6 empty] | Notes | [7 empty] | Notes
Notes | Explanation REQUIRED for 'N/A' measures | [5 empty] | Notes | Explanation REQUIRED for 'N/A' measures | [6 empty] | Notes | Explanation REQUIRED for 'N/A' measures
Notes | [6 empty] | Notes | [7 empty] | Notes
Notes | Explanation REQUIRED for 'N/A' measures | [5 empty] | Notes | Explanation REQUIRED for 'N/A' measures | [6 empty] | Notes | Explanation REQUIRED for 'N/A' measures
Notes | [6 empty] | Notes | [7 empty] | Notes
Notes | Explanation REQUIRED for 'N/A' measures | [5 empty] | Notes | Explanation REQUIRED for 'N/A' measures | [6 empty] | Notes | Explanation REQUIRED for 'N/A' measures
Notes | [6 empty] | Notes | [7 empty] | Notes
Notes | Explanation REQUIRED for 'N/A' measures | [5 empty] | Notes | Explanation REQUIRED for 'N/A' measures | [6 empty] | Notes | Explanation REQUIRED for 'N/A' measures
Notes | [6 empty] | Notes | [7 empty] | Notes
Jump to "Exists"
Jump to "Exists"
Jump to "Add"
Jump to "Modify"
Jump to "Add"
Jump to "Modify"

## FinalReport
Scope of Building Tune-up
Overview of Facility
Areas For Continued Monitoring ("Exists" efficiency measure categories):
Capital Improvement Plan & Timeline (Customer approved measures from "Modify" and "Add" tables)
(ex. Lighting upgrade - common area) |  |  |  | (ex. 3 yrs)
(ex. Boiler upgrade) |  |  |  | (ex. 5 yrs)
Upon completion and approval from PSE, qualified base tune-up incentive payment is equal to: | [6 empty] | 1000
Projected Annual Energy Savings and Incentive Estimates:
| Electric Savings |  | Gas Savings |  | Energy Bill Savings |  | Performance Incentive | $0.05/kWh $0.80/therm
Low Estimate | 50000 | kWh | 222 | therms | 5029.0386 | Low | 177.6
High Estimate | 100000 | kWh | 122 | therms | 9746.0656 | High | 97.6
*Estimate values above reference the IncentiveGoals_4 worksheet. Final performance incentive will be determined by actual savings.
Team Members
Contact |  |  |  | Responsibilities
(First & Last Name), Building Owner |  |  |  | Communicate key tune-up project goals and objectives
Role: | Owner (Tune-up Champion) |  |  | Review final OCx Plan for acceptance
Phone: | (ex. 425.555.5555) |  |  | Review Master List of Findings and approve applicable corrective actions
Email: | (ex. email@email.com) |  |  | Ensures ongoing process is adopted for continued savings
(First & Last Name), Building Engineer |  |  |  | Inform the condition-assessment effort
Role: | Building Operator |  |  | Review and verify Master List of Findings
Phone: | (ex. 425.555.5555) |  |  | Support corrective actions
Email: | (ex. email@email.com) |  |  | Implement itterative process to maintain stable operations
(First & Last Name), Tune-up Provider |  |  |  | Perform Data and analytics review for Master List of Findings
Role: | Tune-up Provider |  |  | Develop and provide Diagnostic Plan
Phone: | (ex. 425.555.5555) |  |  | Transition tune-up into standard operations
Email: | (ex. email@email.com) |  |  | Overall lead for tune-up initiative
(First & Last Name), Energy Engineer |  |  |  | Initial approval for program participation
Role: | Utility Representative |  |  | Review and verify Master List of Findings
Phone: | (ex. 425.555.5555) |  |  | Final documentation review
Email: | (ex. email@email.com) |  |  | Models performance and pays incentive
*Add additional team members and roles as needed.
Building Setpoints
Updates to Sequence of Operations*
*Include original or the new, fully updated sequences in the appendix to this document.
Calibration/Replacement Tracking
Instrument Type |  |  | Make |  | Model | Recommended Calibration Interval*
(ex. CO2 Sensor) |  |  | (ex. Veris) |  | (ex. CW Series) | (ex. 5 years)
(ex. Temperature Sensor) |  |  | (ex. Veris) |  | (ex. TDDAM11) | (ex. No calibration required)
*Include procedures for calibration in appendix.
Appendix A
Measures and Maintenance Tables (Continuous Review)
Appendix B
Calibration Procedures from Calibration/Replacement Table
Appendix C
Sequence of Operations

## MeasureReference (hidden)
**LOCK & HIDE THIS SHEET**
[6 empty] | 0 |  | 0 |  | 0
| Code | Assessment Element | Efficient Operation / Expectation | M&V | Exists Areas | Unique Areas | Modify Areas | Unique Areas | Add Areas | Unique Areas
| 1 | Equipment Scheduling (HVAC, lighting or other) | Title
G1 | 1.01 | Review and match equipment schedules (including daily, weekly, seasonal, day/night, occ./unocc. hours) to occupancy hours. | Schedules match operations and actual building occupancy patterns and are not manually manipulated for morning warmup/cool down. | Screenshot of schedules showing that schedules match occupancy requirements.
| 1.02 | Check for equipment in override/hand mode, no controls for turning off, on/enabled regardless of need. | All functional overrides within front end DDC and at point-of-use are disabled or in automatic mode. | Physically review at point of use and review GUI status display for verification.
G5 | 1.03 | Review occupancy sensors for proper sensing, positioning, and delay period prior to power down. | All lighting wired for occupancy detection powers off after ______ minutes of being unoccupied and does not shutoff when space is occupied. | Physical verification by provider or building staff when space is unoccupied and should be powered down and provide calibration strategy/procedure in the final report.
| 1.04 | Review exterior lighting schedules, light or motion sensors, ensuring that lighting only illuminates with traffic and/or current sunrise/sunset times. | The exterior, controlled lighting is only illuminated when traffic is expected or sensed during periods before sunrise or after sunset. | Physically verify that motion and light sensors operate as expected and provide screenshots of scheduled or a picture of time devise respectively. Provide recommendations for updating schedules as needed in calibration section of final report.
| 1.05 | Review all spaces that incorporate Demand Controlled Ventilation (DCV) and verify calibration of CO2 sensors | All CO2 sensors read ambient ppm when building is unoccupied. | Trend the outside and indoor CO2 sensor readings to verify equal or close to equal values and provide calibration strategy/procedure in the final report.
| _ | Spacer | Title
| 2 | Economizer/Ventilations Loads | Title
| 2.01 | Review the building's ventilation rates used during full heating/cooling (not economizing). | All HVAC units bring in the appropriate amount of ventilation during full-heating/cooling as required by ASHRAE 62.1 standards for appropriate space types | Measure the existing ventilation rates using external loggers or calibrated HVAC unit sensors (OSAT/MAT/RAT) and calculate the required ventilation rates using the sheet in this workbook called "ventilation".
| 2.02 | Verify proper calibration and positioning of MAT/OSAT/RAT sensors. | All temperature sensors are calibrated and positioned in such a way that they report an accurate representation of the expected values and are not affected by other influences (i.e. placed in sun of contacting hot or cold surfaces). | Compare all temperature sensors with known values (e.g. OSAT with outside source, RAT with verified room temperture, MAT with SAT etc.) and provide calibration strategy/procedure in the final report.
| 2.03 | Verify proper calibration and position of the DSP sensor. | Sensor is calibrated and is located at a point in the supply duct to provide a good representation of pressure in all duct work branches. | Physically verify the position of the sensor is appropriate and document the calibration test used to prove sensor works and include in the calibration section of the final report.
| 2.04 | Verify the VFD displayed frequency matches with what the GUI displays. | The two outputs match and verify the modulation of the motor speed. | Physically verify modulation of the motor(s).
| 2.05 | Verify that VAV box dampers modulate as expected MIN/MAX. | Box dampers open and close as expected. | Provide trend of a representative amount of boxes showing modulation of the damper.
| 2.06 | Review economizer usage to maximize free cooling through the use of a dry bulb (changeover) temperature alone. | All AHUs use a changeover temperature of ___°F (min ventilation with mechanical cooling activatates) that matches the RAT or the balance point of the building. | Screenshot of setpoints and trend showing proper operation of economizer (OSAT/Damper position/cooling call)
| 2.07 | Review integrated economizer to maximize free cooling by increasing the economizing temperature to match the RAT and allowing mechanical cooling to supplement cooling during the economizing cycle. | All ventilation unit maximize economizing by matching changeover point to RAT and use an integrated economizer sequencing. | Screenshot of setpoints and trend showing proper operation of economizer (OSAT/Damper position/cooling call)
| _ | Spacer
G8 | 3 | Building Pressurization | Title
| 3.01 | Check for any indications of significant balancing issues (e.g. wind-tunnel effect, ajar or hard to open doors) | Building pressure slightly positive to eliminate infiltration. | Trends of building pressure (if applicable) and/or physical verification of building pressure at each exterior door.
| 3.02 | Verify appropriate position and calibration of building pressure sensors. | Sensors are appropriately calibrated and positioned in representative zone(s) for the building and/or pressure controlled zone(s). | Physically verify positioning of the sensors and calibration per manufacturer's specifications. Record calibration requirements in the sensor calibration section of final report.
| _ | Spacer
G7 | 4 | Controls Problems (HVAC or lighting or other) | Title
| 4.01 | Review BAS for instances of simultaneous heating & cooling | HVAC controls set to reduce or eliminate any unintended or inappropriate simultaneous heating and cooling. | Verify five (5) degree deadband and provide screenshot of representative zones and if applicable, provide BAS screen shots of SAT and DSP reset schedules.
G5 | 4.02 | Review zone deadbands, SAT setpoint(s) and reset schedule for excessive reheat | The supply air temperature is only cooled to meet the minimum cooling load requirements. | Trend the supply air temperature and setpoint and provide screenshot of the reset range.
| 4.03 | Review BAS trending logs for instances of controls hunting, loop tuning opportunities, and/or appropriate dead bands | There is no evidence of setpoints cycling repeatedly to maintain HVAC setpoints. | Review and provide trends of reset setpoints (e.g. pressure, SAT, DAT, HW, CW, etc.).
G6 | 4.04 | Review mapping of control points in the control logic and on graphical user interface (sample of 10% or 20 boxes) | Each point on the DDC GUI represents the correct equipment/state (end-to-end verification). | Physical verification by provider or building staff.
G2 | 4.05 | Review functionality of daylighting controls where applicable | Daylighting controls set or adjusted as appropriate to match actual building illumination patterns | Physically verify using shading devices or time of day variations to observe effect on lighting brightness.
| 4.06 | Review assignment of spaces to each zone, including appropriate schedules and loads | Zone boxes grouped by tenant (or______________________) for scheduling and override. | Screenshot of zone layout from DDC front end if available.
| _ | Spacer
G1 | 5 | Controls - Setpoints | Title
G10 | 5.01 | Review heating & cooling setpoints in each zone against the building's standard setpoints or temp. range. | Zone temperature setpoints for heating and cooling are within building owner requirements at ___°F and ___°F. | Provide document verifying current building requirements and screenshot of setpoint table.
G2 | 5.02 | Review unoccupied and night setback zone temperatures | Night/Unoccupied zone temps meet owner requirements: cooling ___°F or higher; heating ___°F or lower. | Provide trends of zone temperatures and setpoints.
G2 | 5.03 | Review duct static pressure (DSP) setpoint(s) to confirm proper reset range. | DSP setpoint range is 0.5-1.5”, or better (lower). If higher explain what is keeping it at that pressure and not allowing it to go lower. | Provide trend of DSP and setpoint.
G3 | 5.04 | Review deadband between heating & cooling setpoints | Deadband of at least a 5 °F between occupied setpoints and restricts overlap between multiple thermostats in a space. | Review setpoints in each zone.
G3 | 5.05 | Review boiler & chiller lockout temps based on OAT | Boiler plant and cooling lockout on OAT to prevent simultaneous heating and cooling and the temperatures are ___°F and ___°F. | Screenshot of the lockout temperature.
G8 | 5.06 | Review supply air temperature reset schedule in control sequence and/or in BAS settings | SA temperature range is 65-55 °F, or better, with at least 25% delta between SAT and room temperature. | Provide trends of the SAT resetting based on the load.
G2 | 5.07 | Review VAV box max & min airflow settings | Box air flow is within the range specified for each box. | Provide sreenshot from GUI of table that includes VAV box setpoints.
G2 | 5.08 | Review chilled water temperature setpoint | Chilled water setpoint optimized for efficiency as appropriate for building use and occupant needs. | Provide screenshots of chiller plant setpoints.
G4 | 5.09 | Review heating hot water temperature setpoint | Hot water setpoint optimized for efficiency as appropriate for building use and occupant needs. | Provide screenshots of boiler plant setpoints.
| 5.1 | Review Optimum Start settings for optimization | Schedule matches occupancy and allows no more than 4 hours for warmup/cooldown. | Provide trends of OSA damper, fan power, SAT, and DAT for (1) core and (1) perimeter zone.
G2 | 5.11 | Review Optimum Stop settings and functionality | Room temperature heating setpoints gradually adjust down to ___°F and cooling setpoints up to ___°F, 1-2 hours before the scheduled stop. | Provide trends of room temperature and room temperature setpoints.
| _ | Spacer
G6 | 6 | Controls - Sequence optimization | Title
G3 | 6.01 | Compare actual VFD operation with what is required by the sequence of operation commanding modulation. | VFD should modulate as demand increases and decreases. | Provide trends of VFD, SAT, DSP.
| 6.02 | Review SAT reset setpoint schedules and reset control variable | SAT reset is based on a specific temperature range: 65-55°F or better, uses slow reacting trim-and-response sequences, different interval and different controlling variables controlling this and DSP reset. | Provide trends of SAT, OSAT, SAT setpoint, and cooling demand.
| 6.03 | DSP reset based on load | DSP reset is based on load. Low all heating, high all in cooling with reasonable diversity range 0.4-1.5” WC expected, if higher fully document reason. | Provide trend of SF VFD %, DSP setpoint, and DSP.
| 6.04 | HWT reset based on load not OAT. | Based on load and the lowest HWT reset range is in the condensing range (below 140°F) if a condensing boiler. | Provide trend of HW demand, HW setpoint, loop temperature, and boiler enabled.
| 6.05 | CHWT reset based on load not OAT. | CHWT reset of at least 5°F based on zone cooling signals/valves not OSAT and is based on at least two zones excluding cooling only zones or zones with constant load, like equipment rooms. For excluded zones set air/water to meet load at the full reset temp | Provide trends of CHWT (supply and return) and CHWT setpoint.
G3 | 6.06 | Condenser water temperature (CWT) reset based on load | Condenser water temperature (CWT) is reset down to at least 70°F. | Provide trends of OAT, CWT setpoint and supply.
| 6.07 | Review packaged cooling and/or heating staging in the control sequence | All heating and cooling capacity should be gradually enabled according to load within the building and the most efficient operation. | Review the sequence to verify efficient operation of heating and cooling.
| 6.08 | Review chiller staging | Chillers are stage to use the minimal chiller plant energy (i.e. plant kW/ton for cooling tower fans, pumping, chillers) | Review the sequence to verify efficient operation of heating and cooling.
G4 | 6.09 | Review boiler staging | Standard boilers are staged in such a way as to minimize losses from less efficent or oversized boilers; Condensing boilers – low fire first stage and then in parallel from low to high fire. | Review the sequence to verify efficient operation of heating and cooling.
| 6.1 | Review Optimum Start Warm-up capabilities | Optimum start is allowed on for a maximum of 4 hours prior to occupancy. OA closed for warm-up and uses gas pre-heat (if available) with lock out of electric re-heat or other strip heat. | Trend including OSA damper, heating demand, room temp setpoint, fan status, schedule, and room heating setpoint.
G3 | 6.11 | Review Optimum Start Cool-down capabilities | Cool-down use OA with mechanical cooling locked out (ventilation purge 1 hour before pre-cooling) and only boxes not meeting room temperature setpoint are on with primary dampers open. | Trend including OSA damper, cooling demand, room temp setpoint, fan status, schedule, and room heating setpoint.
| 6.12 | Review Optimum Stop (Coast) capabilities | Room temperature heating setpoints are gradually adjusted down and room temperature cooling setpoints up, 1-2 hours before the scheduled stop. | Trends including room temp setpoint, fan status, and schedule.
| 6.13 | Review outside air tempering strategy | OSA is tempered with auxiliary heat only when the OSAT reaches ___°F or if the MAT drops below setpoint. | Review and verify the sequence of operations required for tempering the air.
| 6.14 | Review Demand Controlled Ventilation strategy | Setpoints shall be by space type per ASHRAE Guideline 36. | Provide trend of ppm/OSA damper (not in economizer mode) and/or verify through setpoint manipulation.
| _ | Spacer
| 7 | Equipment Efficiency / Load Reduction | Title
| 7.01 | Review all constant speed fan operation for variability potential | All fans require the maximum CFM supplied by fans and have no variability potential or they are < 7.5 hp. | Provide load calculation supporting constant volume air supply
| 7.02 | Review constant speed pump operation for variable load potential where a VFD could be added or impeller trimming could be implemented | There are no valves throttled down to manually slow water flow, all loads need constant flow of water, or are < 7.5 hp. | Provide load calculation supporting constant GPM supply
H1 | 7.03 | Review non-Condensing HW Boiler equipment for potential replacement with condensing technology. | Equipment is in good repair well inside expected life and has little potential for reducing temperatures below 140°F. | Physical verification by provider or building staff .
| 7.04 | Review DHW equipment for potential replacement with condensing technology. | Equipment is in good repair well inside expected life. | Physical verification by provider or building staff.
G14 | 7.05 | Review lighting levels in all spaces for de-lamping opportunities | Lighting levels appropriate for the space use and occupant needs, dimming or de-lamping where appropriate. | Physical verification by provider or building staff using light meter.
G17 | 7.06 | Review interior or exterior lighting technology for upgrade opportunities to LED or other appropriate technology | All lighting fixtures have recently been replaced. | Physical verification by provider or building staff.
G17 | 7.07 | Identify all interior and exterior lighting fixtures that could be controlled with occupancy, photocells, or schedule that are currently without | All fixtures are controlled to minimize burn hours. | Physical verification by provider or building staff.
| 7.08 | Identify any single zone HVAC systems that could be candidates for DCV control (e.g. conference rooms, gyms, library,etc.). | All AHUs serve multiple zones without a significant oportunity or a diverse occupancy. | Physical verification by provider or building staff.
| 7.09 | Review all packaged equipment for future replacement oportunities and develop a replacement schedule. | All equipment is relatively new and/or in good repair. | Physical verification by provider or building staff.
| _ | Spacer
G11 | 8 | Maintenance | Title
G14 | 8.01 | Check heat exchange surfaces (coils, heat exchangers, fins) | HVAC equipment cleanliness meets ANSI/ASHRAE/ACCA Standard 180‐2012 Table 5‐2, 5‐15 | Physical verification by provider or building staff.
G17 | 8.02 | Review filters & ductwork for any flow obstructions | No obstructions to flow and clean filters | Physical verification by provider or building staff.
G14 | 8.03 | Check dampers, valves, sensors, and actuators functionality | Equipment functions per ANSI/ASHRAE/ACCA Standard 180‐2012 Table 5‐9, 5‐12 | Physical verification by provider or building staff.
| 8.04 | Check steam trap for functionality and leaks | Steam trap functions to standards (ANSI/ASHRAE/ACCA Standard 180‐2012 Table 5‐2, 5‐22). | Physical verification by provider or building staff.
G17 | 8.05 | Review all ducting for gaps or other leakage | Duct leakage minimized to meet standards (ANSI/ASHRAE/ACCA Standard 180‐2012 Table 5‐2, 5‐22). | Physical verification by provider or building staff.
G17 | 8.06 | Check all dampers for leaks when they should be 100% closed | Damper leakage meets ANSI/ASHRAE/ACCA Standard 180‐2012 Table 5‐9, 5‐12. | Physical verification by provider or building staff.
| 8.07 | Check all valves for leakage | Valve leakage meets ANSI/ASHRAE/ACCA Standard 180‐2012 Table 5‐9, 5‐12 if not opening and closing fully. | Physical verification by provider or building staff.
| 8.08 | Review all dampers and actuators located within air handlers and verify that there are no obstructions or failures to prevent modulation. | All dampers modulates as expected with no visible signs of wear or tampering. | Physically verify equipment is in proper working order.
| 8.09 | Review and identify any nuisance or missing alarms, discuss with building staff | All alarms have been addressed and reviewed for potential additions without any sugestions. | Review all alarms with staff, provider, and owner for maximum effectiveness.

## Ventilation (Optional)
Project Name: | [10 empty] | Date(s) of existing measurements: | [7 empty] | Date(s) of final measurements:
TAB DOCUMENTATION FOR MINIMUM OA for AHU SYSTEM | [7 empty] | 2015-10-19
Fill in yellow cells in chart - expand rows to capture all AHUs (HPs, FCUs, RTUs, AHUs).
Document the existing condition. Determine the code requirement. Balance and document the final DDC OA% needed to meet code.
Code OA % needs to match Final OA% within +/- 1%
For final balanced min OA either the temperature method or traverse can be used. Traverse is more accurate for the customer.
Temperature calculation method can only be used if OAT, RAT and MAT accurately reflect these temperatures and there is a 20 F difference between OAT and RAT
|  | EXISTING OA MIN |  |  |  |  | OA MIN REQUIREMENT | [9 empty] | FINAL BALANCED MIN OA
|  | DDC | MEASURED WHEN OA AT MIN (HEATING MODE) |  |  | Calculated OAT* | Area |  |  | Non-People Code |  | People Code |  | TOTAL CODE MIN |  |  | MEASURED WHEN OA AT MIN (HEATING MODE)* |  |  |  | Calculated OAT* | Measured | DDC
EQUIP# | Building | Min OA% stpt | MAT | RAT | OAT | OA% | Type | People density/ 1000 sf ** | sf | cfm/sf *** | Code Min OA Cfm | cfm/ person *** | Code Min OA Cfm | Code Total cfm | Total AHU cfm | Code OA% | MAT | RAT | OAT | Traverse cfm | Final OA% | Traverse OA% | Min OA% stpt
HP-X | 34 | 15% | 66 | 70 | 40 | 13.33% | classroom | 25 | 1500 | 0.12 | 180 | 10 | 375 | 555 | 1500 | 37% | 64 | 70 | 40 | 250 | 20% | 16.67% | 15%
[6 empty] | #DIV/0! |  |  |  |  | 0 |  | 0 | 0 |  | #DIV/0! |  |  |  |  | #DIV/0! | #DIV/0!
[6 empty] | #DIV/0! |  |  |  |  | 0 |  | 0 | 0 |  | #DIV/0! |  |  |  |  | #DIV/0! | #DIV/0!
[6 empty] | #DIV/0! |  |  |  |  | 0 |  | 0 | 0 |  | #DIV/0! |  |  |  |  | #DIV/0! | #DIV/0!
[6 empty] | #DIV/0! |  |  |  |  | 0 |  | 0 | 0 |  | #DIV/0! |  |  |  |  | #DIV/0! | #DIV/0!
[6 empty] | #DIV/0! |  |  |  |  | 0 |  | 0 | 0 |  | #DIV/0! |  |  |  |  | #DIV/0! | #DIV/0!
[6 empty] | #DIV/0! |  |  |  |  | 0 |  | 0 | 0 |  | #DIV/0! |  |  |  |  | #DIV/0! | #DIV/0!
*To use calculated OA; there needs to be 20 F difference between OAT and RAT. OA damper needs to be at min setpoint
Also OAT, RAT and MAT need to accurately reflect these temperatures.
** Can get from WSEC
*** Get from WSEC
Testing Agent Name and Company:
I certify the final minimum outside air was measured and balanced to meet the PSE requirements :
_____________________________________ ___________________________________________________________(signature & date)

## Perf._Changes
Directions: Note changes that have a major impact on energy use but were not a result of the commissioning (CX) process.
Facility: |  | Owner:
Date of This Report: |  | Person Completing Report:
Date of Start of Tune-up Process:
Date of Final Tune-up Report:
Date end of 1st year Performance :
1 | Date or Date Range:
Description of Change or Event (e.g. occupancy changes, new equipment or tenant loads, production schedule, occupied hours etc.)
Describe how the change or event affects energy use. Estimate energy use impact (kWh/year, Therms/yr)
2 | Date or Date Range:
Description of Change or Event (e.g. occupancy changes, new equipment or tenant loads, production schedule, occupied hours etc.)
Describe how the change or event affects energy use. Estimate energy use impact (kWh/year, Therms/yr)
3 | Date or Date Range:
Description of Change or Event (e.g. occupancy changes, new equipment or tenant loads, production schedule, occupied hours etc.)
Describe how the change or event affects energy use. Estimate energy use impact (kWh/year, Therms/yr)
4 | Date or Date Range:
Description of Change or Event (e.g. occupancy changes, new equipment or tenant loads, production schedule, occupied hours etc.)
Describe how the change or event affects energy use. Estimate energy use impact (kWh/year, Therms/yr)

## Imp_Cost
Facility:
1. Only include eligible improvements items. Review guidelines for what is considered an eligible improvement item/expenses and only include items that are eligible
2. Track the cost of implementing the improvements
3. Attach appropriate invoices to match costs for each measure
4. NOTE: if item was already in owner's/ O&M stock
5. NOTE: Up to pre-determined maximum cost is required
6. NOTE: This form can be utilized or the Buidling Tune-Up Specialist can use their own form as long as it includes the fields specified below.
Maximum Required Cost: |  |  | 5000 | Facility sqft: | 50000 | Required $/sqft: | $0.1/sq.ft.
EEI# | Cost ($) | Item in Stock | Description |  |  |  |  | Drop Down Lists
[8 empty] | UPGRADES | PSE $/sqft requirement | PSE utilities
[8 empty] | Y | 0.15 | All PSE
[8 empty] | N | 0.1 | PSE elec (other gas)
0.16
TOTAL | 0 | CUSTOMER IMPLEMENTATION COST